## A1_Summary
Heat Pump Type Register Number | Make | Model | Model Reference | Function | Heat Pump Type | Phases | Voltage (V) | Nominal current (Amps) |  |  |  | Total Heat Pump System (Input) Rated Current (A) | Total Heat Pump System (Input) Rated Power (kVA) | Total Heat Pump System Maximum Demand (A) | Total Heat Pump System Maximum Demand (kVA) | Module Reference | Module | Product Code | Module Input Rated Current (A) | Module Input Rated Power (kVA) | CE Declaration of Conformity |  | Standards Cited on CE Declaration of Conformity |  | Manufacturer's EMC Test Report |  | For Connection Design Purposes, Compliant with |  |  |  | Total Heat Pump System Maximum Demand ≤32A? | Connect & Notify? | Apply to Connect? | Manufacturer's Documentation | Manufacturer's Documentation Declaration |  |  | Refined harmonic data |  |  | Manufacturer's Documentation Declaration |  | External Back-up Heater |  |  | External Supplementary (boost) Heater |  |  | External Water (immersion) Heater
[8 empty] | A-7/W35 | A-7/W45 | A-7/W55 | A-7/W65 | [6 empty] | Product Code |  |  | Filename | Document/Certificate Number | Harmonic Standards | Voltage Fluctuation/ Flicker Standards | Filename | Document Number | Class A limits of IEC 61000-3-2? | Technical Requirements of IEC 61000-3-3? | Both Standards? | Both Standards for All Parts of System? |  |  |  |  | In accordance with EN 61000-3-12 | Ssc min 3-phase (kVA) | Ssc min single-phase (kVA) | Minimum Rsce calculated | Fault level calculated using minimum Rsce (MVA) | Impedance at PCC (Ω) | In accordance with EN 61000-3-11 | Zmax (Ω) | Facility to control via heat pump? | Capable of limiting maximum current? | Maximum current limit (A) | Facility to control via heat pump? | Capable of limiting maximum current? | Maximum current limit (A) | Facility to control via heat pump? | Capable of limiting maximum current? | Maximum current limit (A)
HP_0001 | Daikin | Altherma Monobloc | EDHQ011AA6V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 42 | 9.66 | 42 | 9.66 | EDHQ011AA6V3 | Whole system | EDHQ011A* | 42 | 9.96 | [8 empty] | No | No | No | No | Yes | EEDEN09-720 - 03/2009 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.29
HP_0002 | Daikin | Altherma Monobloc | EDLQ05CAV3+EKMBUHC3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.6 | EDLQ05CAV3 | Heat pump |  | 15.7 | 3.61 | DoC14W900-1Z |  | EN 61000-3-2 | EN 61000-3-3 | 2082543.0551-QUA/EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EKMBUHC3V3 | Back-up heater |  | 13 | 3 | [6 empty] | Yes | Yes | Yes | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_0003 | Daikin | Altherma Monobloc | EDLQ016CV3+EKMBUHC3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.86 | EDLQ016CV3 | Heat pump |  | 34.2 | 7.87 | Doc14W900-1ZU (Rev.1) |  | EN 61000-3-12 | EN 61000-3-11 | 2082543.0551-QUA/EMC |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EKMBUHC3V3 | Back-up heater |  | 13 | 3 | [6 empty] | Yes | Yes | Yes | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_0004 | Daikin | Altherma LT Split | ERGA04DAV3A+EHBH04DA6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 41.8 | 9.614 | 41.8 | 9.61 | ERGA04DAV3A | Heat pump |  | 15.7 | 3.61 | DoC14W900-1ZT |  | EN 61000-3-2 | EN 61000-3-3 | 2192529.0551-EMC |  | Yes | Yes | Yes | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EHBH04DA6V | Back-up heater |  | 26.1 | 6 | [8 empty] | No | No |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_0005 | Daikin | Altherma LT Split | ERLQ016CAV3+EHBH16CB3V | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.86 | ERLQ016CAV3 | Heat pump |  | 34.2 | 7.87 | DoC14W900-1C (Rev.1) |  | EN 61000-3-12 | EN 61000-3-11 | 2024351-QUA/EMC02-4565 |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EHBH16CB3V | Back-up heater |  | 13 | 3 | [6 empty] | Yes | Yes | Yes | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_0006 | Daikin | Altherma | EDLQ05CAV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.611 | 15.7 | 3.611 | EDLQ05CAV3 | Heat pump |  | 15.7 | 3.611 | 1.EDLQ05CAV3 - DoC14W900-1Z | DoC14W900-1Z | EN 61000-3-2 | EN 61000-3-3 | 1.DoC_EDLQ05-07CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0007 | Daikin | Altherma | EDLQ07CAV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.611 | 15.7 | 3.611 | EDLQ07CAV3 | Heat pump |  | 15.7 | 3.611 | 1.EDLQ07CAV3 - DoC14W900-1ZK | DoC14W900-1ZK | EN 61000-3-2 | EN 61000-3-3 | 1.DoC_EDLQ05-07CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0008 | Daikin | Altherma | ERGA04DAV3A + EHBH04DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA04DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBH04DA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0009 | Daikin | Altherma | ERGA06DAV3A + EHBH08DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA06DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBH08DA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0010 | Daikin | Altherma | ERGA08DAV3A + EHBH08DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA08DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBH08DA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0011 | Daikin | Altherma | ERLQ004CAV3 + EHBH04CB3V | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ004CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ004-006CAV3 - DoC14W900-1U | DoC14W900-1U | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBH04CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0012 | Daikin | Altherma | ERLQ006CAV3 + EHBH08CB3V | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ006CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ004-006CAV3 - DoC14W900-1U | DoC14W900-1U | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBH08CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0013 | Daikin | Altherma | ERLQ008CAV3 + EHBH08CB3V | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ008CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ008CAV3 - DoC14W900-1ZN | DoC14W900-1ZN | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBH08CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0014 | Daikin | Altherma | ERLQ004CAV3 + EHVH04SU18CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ004CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ004-006CAV3 - DoC14W900-1U | DoC14W900-1U | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHVH04SU18CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0015 | Daikin | Altherma | ERLQ006CAV3 + EHVH08SU18CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ006CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ004-006CAV3 - DoC14W900-1U | DoC14W900-1U | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHVH08SU18CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0016 | Daikin | Altherma | ERLQ008CAV3 + EHVH08SU18CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ008CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ008CAV3 - DoC14W900-1ZN | DoC14W900-1ZN | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHVH08SU18CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0017 | Daikin | Altherma | ERLQ006CAV3 + EHVH08SU26CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ006CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ004-006CAV3 - DoC14W900-1U | DoC14W900-1U | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHVH08SU26CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0018 | Daikin | Altherma | ERLQ008CAV3 + EHVH08SU26CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | ERLQ008CAV3 | Heat pump |  | 15.7 | 3.611 | 5.DoC_ERLQ008CAV3 - DoC14W900-1ZN | DoC14W900-1ZN | EN 61000-3-2 | EN 61000-3-3 | 5a.DoC_ERLQ04-08CAV3_EMC |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHVH08SU26CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0019 | Daikin | Altherma | EVLQ05CAV3 + EHYHBH05AAV32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.611 | 15.7 | 3.611 | EVLQ05CAV3 | Heat pump |  | 15.7 | 3.611 | 3.EVLQ05CAV3 - DoC14W900-1W.pdf | DoC14W900-1W | EN 61000-3-2 | EN 61000-3-3 | 3a.DoC_EVLQ-CAV3_EMC.pdf |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHYHBH05AAV32 | Heat pump |  | 0 | 0 | N/A | N/A | EN 61000-3-2 | EN 61000-3-3 | 3b.DoC_EHYHBH05-08AAV32_EMC.pdf |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0020 | Daikin | Altherma | EVLQ08CAV3 + EHYHBH08AAV32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.611 | 15.7 | 3.611 | EVLQ08CAV3 | Heat pump |  | 15.7 | 3.611 | 3.EVLQ08CAV3 - DoC14W900-1ZM | DoC14W900-1ZM | EN 61000-3-2 | EN 61000-3-3 | 3a.DoC_EVLQ-CAV3_EMC.pdf |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHYHBH08AAV32 | Heat pump |  | 0 | 0 | N/A | N/A | EN 61000-3-2 | EN 61000-3-3 | 3b.DoC_EHYHBH05-08AAV32_EMC.pdf |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0021 | Daikin | Altherma | ERLQ011CAV3 + EHBH11CB3V | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ011CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.223 | 0.238 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHBH11CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0022 | Daikin | Altherma | ERLQ014CAV3 + EHBH16CB3V | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ014CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.223 | 0.238 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHBH16CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0023 | Daikin | Altherma | ERLQ016CAV3 + EHBH16CB3V | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ016CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.223 | 0.238 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHBH16CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0024 | Daikin | Altherma | ERLQ011CAV3 + EHVH11SU26CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ011CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHVH11SU26CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5b.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0025 | Daikin | Altherma | ERLQ014CAV3 + EHVH16SU26CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ014CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHVH16SU26CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5b.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0026 | Daikin | Altherma | ERLQ016CAV3 + EHVH16SU26CB6W | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ016CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHVH16SU26CB6W | Back-up heater - on-board |  | 13 | 2.99 | 5b.DoC_EHVH-SU-CBW6_DoC14W900-1ZP | DoC14W900-1ZP | EN 61000-3-2 | EN 61000-3-3 | 5b.DoC_EHVH-SU-CB6W_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0027 | Daikin | Altherma | EBLQ011CAV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 34.2 | 7.87 | 34.2 | 7.87 | EBLQ011CAV3 | Heat pump |  | 34.2 | 7.87 | 2.EDLQ011-016CAV3 - DoC14W900-1Z | DoC14W900-1ZU | EN 61000-3-12 | EN 61000-3-11 | 2225268.0501-EMC | 2225268.0501-EMC | No | No | No | No | No | No | Yes | 2225268.0501-EMC | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976 | No |  |  | No |  |  | No
HP_0028 | Daikin | Altherma | EBLQ014CAV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 34.2 | 7.87 | 34.2 | 7.87 | EBLQ014CAV3 | Heat pump |  | 34.2 | 7.87 | 2.EDLQ011-016CAV3 - DoC14W900-1Z | DoC14W900-1ZU | EN 61000-3-12 | EN 61000-3-11 | 2225268.0501-EMC | 2225268.0501-EMC | No | No | No | No | No | No | Yes | 2225268.0501-EMC | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976 | No |  |  | No |  |  | No
HP_0029 | Daikin | Altherma | EBLQ016CAV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 34.2 | 7.87 | 34.2 | 7.87 | EBLQ016CAV3 | Heat pump |  | 34.2 | 7.87 | 2.EDLQ011-016CAV3 - DoC14W900-1Z | DoC14W900-1ZU | EN 61000-3-12 | EN 61000-3-11 | 2225268.0501-EMC | 2225268.0501-EMC | No | No | No | No | No | No | Yes | 2225268.0501-EMC | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976 | No |  |  | No |  |  | No
HP_0030 | Daikin | Altherma | EDLQ011CAV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 34.2 | 7.87 | 34.2 | 7.87 | EDLQ011CAV3 | Heat pump |  | 34.2 | 7.87 | 2.EDLQ011-016CAV3 - DoC14W900-1Z | DoC14W900-1ZU | EN 61000-3-12 | EN 61000-3-11 | 2225268.0501-EMC | 2225268.0501-EMC | No | No | No | No | No | No | Yes | 2225268.0501-EMC | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976 | No |  |  | No |  |  | No
HP_0031 | Daikin | Altherma | EDLQ014CAV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 34.2 | 7.87 | 34.2 | 7.87 | EDLQ014CAV3 | Heat pump |  | 34.2 | 7.87 | 2.EDLQ011-016CAV3 - DoC14W900-1Z | DoC14W900-1ZU | EN 61000-3-12 | EN 61000-3-11 | 2225268.0501-EMC | 2225268.0501-EMC | No | No | No | No | No | No | Yes | 2225268.0501-EMC | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976 | No |  |  | No |  |  | No
HP_0032 | Daikin | Altherma | EDLQ016CAV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 34.2 | 7.87 | 34.2 | 7.87 | EDLQ016CAV3 | Heat pump |  | 34.2 | 7.87 | 2.EDLQ011-016CAV3 - DoC14W900-1Z | DoC14W900-1ZU | EN 61000-3-12 | EN 61000-3-11 | 2225268.0501-EMC | 2225268.0501-EMC | No | No | No | No | No | No | Yes | 2225268.0501-EMC | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976 | No |  |  | No |  |  | No
HP_0033 | Daikin | Altherma | EBLQ011CAW1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EBLQ011CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212 | No |  |  | No |  |  | No
HP_0034 | Daikin | Altherma | EBLQ014CAW1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EBLQ014CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212 | No |  |  | No |  |  | No
HP_0035 | Daikin | Altherma | EBLQ016CAW1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EBLQ016CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212 | No |  |  | No |  |  | No
HP_0036 | Daikin | Altherma | EDLQ011CAW1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EDLQ011CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212 | No |  |  | No |  |  | No
HP_0037 | Daikin | Altherma | EDLQ014CAW1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EDLQ014CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212 | No |  |  | No |  |  | No
HP_0038 | Daikin | Altherma | EDLQ016CAW1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EDLQ016CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212 | No |  |  | No |  |  | No
HP_0039 | Daikin | Altherma | EJHA04AAV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.611 | 15.7 | 3.611 | EJHA04AAV3 | Heat pump |  | 15.7 | 3.611 | 4.EJHA04AAV3_DoC14W900-2AF.pdf | DoC14W900-2AF | EN 61000-3-2 | EN 61000-3-3 | 2230920.0501-EMC | 2230920.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0040 | Daikin | Altherma | EPGA11DAV3+EABH16DA6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA11DAV3 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | No | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EABH16DA6V | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0041 | Daikin | Altherma | EPGA11DAV3+EABX16DA6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA11DAV3 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | No | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EABX16DA6V | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0042 | Daikin | Altherma | EPGA14DAV3+EABH16DA6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA14DAV3 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | No | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EABH16DA6V | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0043 | Daikin | Altherma | EPGA14DAV3+EABX16DA6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA14DAV3 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | No | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EABX16DA6V | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0044 | Daikin | Altherma | EPGA16DAV3+EABH16DA6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA16DAV3 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | No | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EABH16DA6V | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0045 | Daikin | Altherma | EPGA16DAV3+EABX16DA6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA16DAV3 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | No | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EABX16DA6V | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0046 | Daikin | Altherma | EBLQ011CAV3+EKMBUHCA3V3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.86 | 47.2 | 10.86 | EBLQ011CAV3 | Heat pump |  | 34.2 | 7.87 | 2.DoC_EDLQ011-016CAV3_EMC | 3PW57792-15J | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976
[16 empty] | EKMBUHCA3V3 | Back-up heater - external |  | 13 | 3 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0047 | Daikin | Altherma | EBLQ014CAV3+EKMBUHCA3V3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.86 | 47.2 | 10.87 | EBLQ014CAV3 | Heat pump |  | 34.2 | 7.87 | 2.DoC_EDLQ011-016CAV3_EMC | 3PW57792-15J | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976
[16 empty] | EKMBUHCA3V3 | Back-up heater - external |  | 13 | 3 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0048 | Daikin | Altherma | EBLQ016CAV3+EKMBUHCA3V3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.86 | 47.2 | 10.87 | EBLQ016CAV3 | Heat pump |  | 34.2 | 7.87 | 2.DoC_EDLQ011-016CAV3_EMC | 3PW57792-15J | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976
[16 empty] | EKMBUHCA3V3 | Back-up heater - external |  | 13 | 3 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0049 | Daikin | Altherma | EDLQ011CAV3+EKMBUHCA3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.86 | 47.2 | 10.86 | EDLQ011CAV3 | Heat pump |  | 34.2 | 7.87 | 2.DoC_EDLQ011-016CAV3_EMC | 3PW57792-15J | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976
[16 empty] | EKMBUHCA3V3 | Back-up heater - external |  | 13 | 3 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0050 | Daikin | Altherma | EDLQ014CAV3+EKMBUHCA3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.86 | 47.2 | 10.86 | EDLQ014CAV3 | Heat pump |  | 34.2 | 7.87 | 2.DoC_EDLQ011-016CAV3_EMC | 3PW57792-15J | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976
[16 empty] | EKMBUHCA3V3 | Back-up heater - external |  | 13 | 3 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0051 | Daikin | Altherma | EDLQ016CAV3+EKMBUHCA3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.86 | 47.2 | 10.86 | EDLQ016CAV3 | Heat pump |  | 34.2 | 7.87 | 2.DoC_EDLQ011-016CAV3_EMC | 3PW57792-15J | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1350 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2976
[16 empty] | EKMBUHCA3V3 | Back-up heater - external |  | 13 | 3 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | 2228784.0501-EMC | 2228784.0501-EMC | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0052 | Daikin | Altherma | EPRA14DV3+ETBH16D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPRA14DV3+ETBH16D6V | Whole system |  | 48.1 | 11.06 | DoC14W900-2AL_1PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AL & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0053 | Daikin | Altherma | EPRA14DV3+ETBX16D6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPRA14DV3+ETBX16D6V | Whole system |  | 48.1 | 11.06 | DoC14W900-2AL_1PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AL & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0054 | Daikin | Altherma | EPRA16DV3+ETBX16D6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPRA16DV3+ETBX16D6V | Whole system |  | 48.1 | 11.06 | DoC14W900-2AL_1PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AL & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0055 | Daikin | Altherma | EPRA16DV3+ETBH16D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPRA16DV3+ETBH16D6V | Whole system |  | 48.1 | 11.06 | DoC14W900-2AL_1PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AL & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0056 | Daikin | Altherma | EPRA18DV3+ETBH16D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPRA18DV3+ETBH16D6V | Whole system |  | 48.1 | 11.06 | DoC14W900-2AL_1PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AL & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0057 | Daikin | Altherma | EPRA18DV3+ETBX16D6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPRA18DV3+ETBX16D6V | Whole system |  | 48.1 | 11.06 | DoC14W900-2AL_1PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AL & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0058 | Daikin | Altherma | EPRA14DW1 + ETBH16D6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 30.4 | 21.06 | 30.4 | 21.06 | EPRA14DW1 + ETBH16D6V | Whole system |  | 30.4 | 23.14 | DoC14W900-2AM_3PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AM & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0059 | Daikin | Altherma | EPRA14DW1 + ETBH16D9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | EPRA14DW1 + ETBH16D9W | Whole system |  | 26 | 20.09 | DoC14W900-2AM_3PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AM & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0060 | Daikin | Altherma | EPRA14DW1 + ETBX16D6V | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 30.4 | 21.06 | 30.4 | 21.06 | EPRA14DW1 + ETBX16D6V | Whole system |  | 30.4 | 13.6 | DoC14W900-2AM_3PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AM & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0061 | Daikin | Altherma | EPRA14DW1 + ETBX16D9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | EPRA14DW1 + ETBX16D9W | Whole system |  | 26 | 20.09 | DoC14W900-2AM_3PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AM & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0062 | Daikin | Altherma | EPRA16DW1 + ETBH16D6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 30.4 | 21.06 | 30.4 | 21.06 | EPRA16DW1 + ETBH16D6V | Whole system |  | 30.4 | 13.6 | DoC14W900-2AM_3PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AM & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0063 | Daikin | Altherma | EPRA16DW1 + ETBH16D9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | EPRA16DW1 + ETBH16D9W | Whole system |  | 26 | 20.09 | DoC14W900-2AM_3PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AM & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0064 | Daikin | Altherma | EPRA16DW1 + ETBX16D6V | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 30.4 | 21.06 | 30.4 | 21.06 | EPRA16DW1 + ETBX16D6V | Whole system |  | 30.4 | 13.6 | DoC14W900-2AM_3PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AM & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0065 | Daikin | Altherma | EPRA16DW1 + ETBX16D9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | EPRA16DW1 + ETBX16D9W | Whole system |  | 26 | 20.09 | DoC14W900-2AM_3PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AM & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0066 | Daikin | Altherma | EPRA18DW1 + ETBH16D6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 30.4 | 21.06 | 30.4 | 21.06 | EPRA18DW1 + ETBH16D6V | Whole system |  | 30.4 | 13.6 | DoC14W900-2AM_3PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AM & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0067 | Daikin | Altherma | EPRA18DW1 + ETBX16D6V | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 30.4 | 21.06 | 30.4 | 21.06 | EPRA18DW1 + ETBX16D6V | Whole system |  | 30.4 | 13.6 | DoC14W900-2AM_3PH_OU & DoC14W900-2AN_1PH_IU | DoC14W900-2AM & DoC14W900-2AN | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0068 | Daikin | Altherma | EPRA18DW1 + ETBX16D9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | EPRA18DW1 + ETBX16D9W | Whole system |  | 26 | 20.09 | DoC14W900-2AM_3PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AM & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0069 | Daikin | Altherma | EPRA18DW1 + ETBH16D9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | EPRA18DW1 + ETBH16D9W | Whole system |  | 26 | 20.09 | DoC14W900-2AM_3PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AM & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0070 | Daikin | Altherma | EPRA14DV3+ETBH16D9W | Heating only | Air Source | 1 | 230 |  |  |  |  | 43.7 | 10.05 | 43.7 | 10.05 | EPRA14DV3+ETBH16D9W | Whole system |  | 43.7 | 10.05 | DoC14W900-2AL_1PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AL & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0071 | Daikin | Altherma | EPRA14DV3+ETBX16D9W | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 43.7 | 10.05 | 43.7 | 10.05 | EPRA14DV3+ETBX16D9W | Whole system |  | 43.7 | 10.05 | DoC14W900-2AL_1PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AL & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0072 | Daikin | Altherma | EPRA16DV3+ETBH16D9W | Heating only | Air Source | 1 | 230 |  |  |  |  | 43.7 | 10.05 | 43.7 | 10.05 | EPRA16DV3+ETBH16D9W | Whole system |  | 43.7 | 10.05 | DoC14W900-2AL_1PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AL & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0073 | Daikin | Altherma | EPRA16DV3+ETBX16D9W | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 43.7 | 10.05 | 43.7 | 10.05 | EPRA16DV3+ETBX16D9W | Whole system |  | 43.7 | 10.05 | DoC14W900-2AL_1PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AL & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0074 | Daikin | Altherma | EPRA18DV3+ETBH16D9W | Heating only | Air Source | 1 | 230 |  |  |  |  | 43.7 | 10.05 | 43.7 | 10.05 | EPRA18DV3+ETBH16D9W | Whole system |  | 43.7 | 10.05 | DoC14W900-2AL_1PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AL & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0075 | Daikin | Altherma | EPRA18DV3+ETBX16D9W | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 43.7 | 10.05 | 43.7 | 10.05 | EPRA18DV3+ETBX16D9W | Whole system |  | 43.7 | 10.05 | DoC14W900-2AL_1PH_OU & DoC14W900-2AP_3PH_IU | DoC14W900-2AL & DoC14W900-2AP | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0076 | Daikin | Altherma | EGSAX10UDA9W | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 4.9 | 1.13 | 15.5 | 3.57 | EGSAX10UDA9W | Heat pump |  | 4.9 | 1.12 | DoC14W900-2AV.pdf | DoC14W900-2AV | EN 61000-3-2 | EN 61000-3-3 | 2234882.0501-EMC.pdf | 2234882.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0077 | Daikin | Altherma | EGSAX06UDA9W | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 3.04 | 0.7 | 15.5 | 3.57 | EGSAX06UDA9W | Heat pump |  | 3.04 | 0.7 | DoC14W900-2AV.pdf | DoC14W900-2AV | EN 61000-3-2 | EN 61000-3-3 | 2234882.0501-EMC.pdf | 2234882.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0078 | Daikin | Altherma | EGSAH10UDA9W | Heating only | Ground Source | 1 | 230 |  |  |  |  | 4.9 | 1.13 | 15.5 | 3.57 | EGSAH10UDA9W | Heat pump |  | 4.9 | 1.12 | DoC14W900-2AV.pdf | DoC14W900-2AV | EN 61000-3-2 | EN 61000-3-3 | 2234882.0501-EMC.pdf | 2234882.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0079 | Daikin | Altherma | EGSAH06UDA9W | Heating only | Ground Source | 1 | 230 |  |  |  |  | 3.04 | 0.7 | 15.5 | 3.57 | EGSAH06UDA9W | Heat pump |  | 3.04 | 0.7 | DoC14W900-2AV.pdf | DoC14W900-2AV | EN 61000-3-2 | EN 61000-3-3 | 2234882.0501-EMC.pdf | 2234882.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0080 | Daikin | Altherma | EPGA11DAV3 + EAVH16SU18D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA11DAV3 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EAVH16SU18D6V | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0081 | Daikin | Altherma | EPGA11DAV3 + EAVH16SU23D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA11DAV3 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EAVH16SU23D6V | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0082 | Daikin | Altherma | EPGA14DAV3 + EAVH16SU18D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA14DAV3 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EAVH16SU18D6V | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0083 | Daikin | Altherma | EPGA14DAV3 + EAVH16SU23D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA14DAV3 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EAVH16SU23D6V | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0084 | Daikin | Altherma | EPGA16DAV3 + EAVH16SU18D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA16DAV3 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EAVH16SU18D6V | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0085 | Daikin | Altherma | EPGA16DAV3 + EAVH16SU23D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.1 | 11.06 | 48.1 | 11.06 | EPGA16DAV3 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EAVH16SU23D6V | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0086 | Daikin | Altherma | EBLA16DA3V37 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EBLA16DA3V37 | Heat pump |  | 28.887 | 6.644 | Doc14W900-2BB.PDF | Doc14W900-2BB | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0087 | Daikin | Altherma | EDLA16DA3V37 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EDLA16DA3V37 | Heat pump |  | 28.887 | 6.644 | Doc14W900-2BB.PDF | Doc14W900-2BB | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0088 | Daikin | Altherma | EDLA14DA3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EDLA14DA3V3 | Heat pump |  | 28.887 | 6.644 | Doc14W900-2BB.PDF | Doc14W900-2BB | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0089 | Daikin | Altherma | EDLA09DA3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EDLA09DA3V3 | Heat pump |  | 28.887 | 6.644 | Doc14W900-2BB.PDF | Doc14W900-2BB | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0090 | Daikin | Altherma | EBLA14DA3V3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EBLA14DA3V3 | Heat pump |  | 28.887 | 6.644 | Doc14W900-2BB.PDF | Doc14W900-2BB | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0091 | Daikin | Altherma | EBLA09DA3V3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EBLA09DA3V3 | Heat pump |  | 28.887 | 6.644 | Doc14W900-2BB.PDF | Doc14W900-2BB | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0092 | Daikin | Altherma | EBLQ07CAV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.61 | 15.7 | 3.61 | EBLQ07CAV3 | Heat pump |  | 15.7 | 3.611 | 1.EDLQ07CAV3 - DoC14W900-1ZK | DoC14W900-1ZK | EN 61000-3-2 | EN 61000-3-3 | TCF025H_(D4x)H17_testreport_Monoblock_har.pdf | TCF025H_(D4x)H17 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0093 | Daikin | Altherma | EBLQ05CAV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.61 | 15.7 | 3.61 | EBLQ05CAV3 | Heat pump |  | 15.7 | 3.611 | 1.EDLQ05CAV3 - DoC14W900-1Z | DoC14W900-1Z | EN 61000-3-2 | EN 61000-3-3 | TCF025H_(D4x)H17_testreport_Monoblock_har.pdf | TCF025H_(D4x)H17 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0094 | Daikin | Altherma | EBLQ011CAW1+EKMBUHCA9W1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.9 | 17.25 | 24.9 | 17.25 | EBLQ011CAW1+EKMBUHCA9W1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[16 empty] | EKMBUHCA9W1 | Back-up heater - external |  | 8.6 | 6 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0095 | Daikin | Altherma | EBLQ014CAW1+EKMBUHCA9W1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.9 | 17.25 | 24.9 | 17.25 | EBLQ014CAW1+EKMBUHCA9W1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[16 empty] | EKMBUHCA9W1 | Back-up heater - external |  | 8.6 | 6 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0096 | Daikin | Altherma | EBLQ016CAW1+EKMBUHCA9W1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.9 | 17.25 | 24.9 | 17.25 | EBLQ016CAW1+EKMBUHCA9W1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[16 empty] | EKMBUHCA9W1 | Back-up heater - external |  | 8.6 | 6 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0097 | Daikin | Altherma | EDLQ011CAW1+EKMBUHCA9W1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 24.9 | 17.25 | 24.9 | 17.25 | EDLQ011CAW1+EKMBUHCA9W1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[16 empty] | EKMBUHCA9W1 | Back-up heater - external |  | 8.6 | 6 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0098 | Daikin | Altherma | EDLQ014CAW1+EKMBUHCA9W1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 24.9 | 17.25 | 24.9 | 17.25 | EDLQ014CAW1+EKMBUHCA9W1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[16 empty] | EKMBUHCA9W1 | Back-up heater - external |  | 8.6 | 6 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0099 | Daikin | Altherma | EDLQ016CAW1+EKMBUHCA9W1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 24.9 | 17.25 | 24.9 | 17.25 | EDLQ016CAW1+EKMBUHCA9W1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[16 empty] | EKMBUHCA9W1 | Back-up heater - external |  | 8.6 | 6 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-12 | EN 61000-3-11 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Daikin DERH EKMBUHCA9W1 Flicker Calc_v1 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2801 | Daikin | Altherma | EDLQ07CAV3 + EKMBUHCA3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.7 | 6.601 | 28.7 | 6.601 | EDLQ07CAV3 | Heat pump |  | 15.7 | 3.611 | 1.EDLQ07CAV3 - DoC14W900-1ZK | DoC14W900-1ZK | EN 61000-3-2 | EN 61000-3-3 | TCF025H_(D4x)H17_testreport_Monoblock_har.pdf | TCF025H_(D4x)H17 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EKMBUHCA3V3 | Back-up heater - external |  | 13 | 2.99 | DOC14W900-2AK | DoC14W900-2AK | EN 61000-3-2 | EN 61000-3-3 | 2228784.0501-EMC | 2228784.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2802 | Daikin | Altherma | EBLA11DA3V3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EBLA11DA3V3 | Heat pump |  | 28.887 | 6.644 | DoC14W900-2BB Rev 1.pdf | Doc14W900-2BB Rev 1 | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_2803 | Daikin | Altherma | EDLA11DA3V3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.887 | 6.644 | 28.887 | 6.644 | EDLA11DA3V3 | Heat pump |  | 28.887 | 6.644 | DoC14W900-2BB Rev 1.pdf | Doc14W900-2BB Rev 1 | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4h)A11_2245632.0501-EMC.pdf | 2245632.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.11339 | 0.467 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_2804 | Daikin | Altherma | EBLA09DA3W1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EBLA09DA3W1 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EBLA09DA3W1 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EBLA09DA3W1 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2805 | Daikin | Altherma | EBLA11DA3W1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EBLA11DA3W1 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EBLA11DA3W1 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EBLA11DA3W1 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2806 | Daikin | Altherma | EBLA14DA3W1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EBLA14DA3W1 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EBLA14DA3W1 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EBLA14DA3W1 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2807 | Daikin | Altherma | EBLA16DA3W17 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EBLA16DA3W17 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EBLA16DA3W17 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EBLA16DA3W17 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2808 | Daikin | Altherma | EDLA09DA3W1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EDLA09DA3W1 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EDLA09DA3W1 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EDLA09DA3W1 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2809 | Daikin | Altherma | EDLA11DA3W1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EDLA11DA3W1 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EDLA11DA3W1 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EDLA11DA3W1 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2810 | Daikin | Altherma | EDLA14DA3W1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EDLA14DA3W1 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EDLA14DA3W1 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EDLA14DA3W1 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2811 | Daikin | Altherma | EDLA16DA3W17 | Heating only | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | EDLA16DA3W17 | Heat pump |  | 14 | 9.7 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
|  |  | EDLA16DA3W17 BUH |  |  | 1 | 230 |  |  |  |  | 13 | 2.99 |  |  | EDLA16DA3W17 BUH | Back-up heater - on-board |  | 13 | 3 | DoC14W900-2BC Rev 1.pdf | DoC14W900-2BC Rev 1 | EN 61000-3-2 | EN 61000-3-3 | 2247512.0501-EMC.pdf | 2247512.0501-EMC | Yes | Yes | Yes |  |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2812 | Daikin | Altherma | ERGA04EAV3A+EHVH04SU18EA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA04EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH04SU18EA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2813 | Daikin | Altherma | ERGA04EAV3A+EHVH04SU23EA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA04EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH04SU23EA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2814 | Daikin | Altherma | ERGA06EAV3A+EHVH08SU18EA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA06EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU18EA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2815 | Daikin | Altherma | ERGA06EAV3A+EHVH08SU23EA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA06EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU23EA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2816 | Daikin | Altherma | ERGA08EAV3A+EHVH08SU18EA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA08EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU18EA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2817 | Daikin | Altherma | ERGA08EAV3A+EHVH08SU23EA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA08EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU23EA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2818 | Daikin | Altherma | ERGA04EAV3A+EHBH04EA6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA04EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHBH04EA6V | Back-up heater - external |  | 8.7 | 2 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2819 | Daikin | Altherma | ERGA04EAV3A+EHBX04EA6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA04EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHBX04EA6V | Back-up heater - external |  | 8.7 | 2 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2820 | Daikin | Altherma | ERGA06EAV3A+EHBH08EA6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA06EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHBH06EA6V | Back-up heater - external |  | 8.7 | 2 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2821 | Daikin | Altherma | ERGA06EAV3A+EHBX08EA6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA06EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHBX08EA6V | Back-up heater - external |  | 8.7 | 2 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2822 | Daikin | Altherma | ERGA08EAV3A+EHBH08EA6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA08EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHBH08EA6V | Back-up heater - external |  | 8.7 | 2 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2823 | Daikin | Altherma | ERGA08EAV3A+EHBX08EA6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA08EAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHBX08EA6V | Back-up heater - external |  | 8.7 | 2 | DoC14W900-2BL | DoC14W900-2BL | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2824 | Daikin | Altherma | ERGA04DAV3A + EHBX04DA6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA04DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBX04DA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_2825 | Daikin | Altherma | ERGA06DAV3A + EHBX08DA6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA06DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBX08DA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_2826 | Daikin | Altherma | ERGA08DAV3A + EHBX08DA6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | ERGA08DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | EHBX08DA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_2827 | Daikin | Altherma | ERGA04DAV3A+EHVH04SU18DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA04DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH04SU18DA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2828 | Daikin | Altherma | ERGA04DAV3A+EHVH04SU23DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA04DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH04SU23DA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2829 | Daikin | Altherma | ERGA06DAV3A+EHVH08SU18DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA06DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU18DA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2830 | Daikin | Altherma | ERGA06DAV3A+EHVH08SU23DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA06DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU23DA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2831 | Daikin | Altherma | ERGA08DAV3A+EHVH08SU18DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA08DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU18DA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2832 | Daikin | Altherma | ERGA08DAV3A+EHVH08SU23DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 28.9 | 6.65 | 28.9 | 6.65 | ERGA08DAV3A | Heat pump |  | 15.9 | 3.66 | DoI14W900-1B Rev 1_signed | DoI14W900-1B (Rev 1) | EN 61000-3-2 | EN 61000-3-3 | S15Z2601 | S15Z2601 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EHVH08SU23DA6V | Back-up heater - external |  | 13 | 2.99 | DoC14W900-2BK | DoC14W900-2BK | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2833 | Daikin | Altherma | EPRA14DAW1+ETBX16EF9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA14DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | ETBX16EF9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4b)A1_2251393.0501-EMC.pdf | 2251393.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2834 | Daikin | Altherma | EPRA14DAW1+ETBH16EF9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA14DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | ETBH16EF9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4b)A1_2251393.0501-EMC.pdf | 2251393.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2835 | Daikin | Altherma | EPRA16DAW1+ETBX16EF9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA16DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | ETBX16EF9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4b)A1_2251393.0501-EMC.pdf | 2251393.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2836 | Daikin | Altherma | EPRA16DAW1+ETBH16EF9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA16DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | ETBH16EF9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4b)A1_2251393.0501-EMC.pdf | 2251393.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2837 | Daikin | Altherma | EPRA18DAW1+ETBX16EF9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA18DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | ETBX16EF9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4b)A1_2251393.0501-EMC.pdf | 2251393.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2838 | Daikin | Altherma | EPRA18DAW1+ETBH16EF9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA18DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | ETBH16EF9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4b)A1_2251393.0501-EMC.pdf | 2251393.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2839 | Daikin | Altherma | EPRA14DAW1+ETVH16SU18EA6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA14DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[6 empty] | 1 | 230 | [8 empty] | ETVH16SU18EA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2840 | Daikin | Altherma | EPRA14DAW1+ETVH16SU23EA6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA14DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[6 empty] | 1 | 230 | [8 empty] | ETVH16SU23EA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2841 | Daikin | Altherma | EPRA16DAW1+ETVH16SU18EA6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA16DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[6 empty] | 1 | 230 | [8 empty] | ETVH16SU18EA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2842 | Daikin | Altherma | EPRA16DAW1+ETVH16SU23EA6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA16DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[6 empty] | 1 | 230 | [8 empty] | ETVH16SU23EA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2843 | Daikin | Altherma | EPRA18DAW1+ETVH16SU18EA6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA18DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[6 empty] | 1 | 230 | [8 empty] | ETVH16SU18EA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2844 | Daikin | Altherma | EPRA18DAW1+ETVH16SU23EA6V | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA18DAW1 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU.pdf | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC.pdf | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[6 empty] | 1 | 230 | [8 empty] | ETVH16SU23EA6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2845 | Daikin | Altherma | EPRA14DV3+ETBH16E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA14DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETBH16E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2846 | Daikin | Altherma | EPRA14DV3+ETBX16E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA14DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETBX16E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2847 | Daikin | Altherma | EPRA16DV3+ETBH16E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA16DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETBH16E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2848 | Daikin | Altherma | EPRA16DV3+ETBX16E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA16DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETBX16E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2849 | Daikin | Altherma | EPRA18DV3+ETBH16E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA18DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETBH16E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2850 | Daikin | Altherma | EPRA18DV3+ETBX16E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA18DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETBX16E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM.pdf | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2851 | Daikin | Altherma | EPRA14DV3+ETVH16SU18E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA14DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETVH16SU18E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2852 | Daikin | Altherma | EPRA14DV3+ETVH16SU23E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA14DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETVH16SU23E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2853 | Daikin | Altherma | EPRA16DV3+ETVH16SU18E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA16DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETVH16SU18E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2854 | Daikin | Altherma | EPRA16DV3+ETVH16SU23E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA16DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETVH16SU23E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2855 | Daikin | Altherma | EPRA18DV3+ETVH16SU18E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA18DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETVH16SU18E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2856 | Daikin | Altherma | EPRA18DV3+ETVH16SU23E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.612 | 24.4 | 5.61 | EPRA14DV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2AL Rev 1.pdf | DoC14W900-2AL (Rev 1) | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | ETVH16SU18E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN.pdf | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2857 | Daikin | Altherma | ERLQ011CAV3 + EHBX11CB3V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ011CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHBX11CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_2858 | Daikin | Altherma | ERLQ014CAV3 + EHBX16CB3V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ014CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHBX16CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_2859 | Daikin | Altherma | ERLQ016CAV3 + EHBX16CB3V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.2 | 10.856 | 47.2 | 10.856 | ERLQ016CAV3 | Heat pump |  | 34.2 | 7.866 | 6.ERLQ011-016 - DoC14W900-1C Rev 1.pdf | DoC14W900-1C Rev 1 | EN 61000-3-12 | EN 61000-3-11 | 6.DoC_ERLQ011-016CAV3_EMC.pdf |  | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | EHBX16CB3V | Back-up heater - on-board |  | 13 | 2.99 | 5.DoC_EHBH-CB - DoC14W900-1S | DoC14W900-1S | EN 61000-3-2 | EN 61000-3-3 | 5c.DoC_EHBH-CB_EMC |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_2860 | Daikin | Altherma | ERLA11DV3 + EBBX11D6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.8 | 7.08 | 30.8 | 7.08 | ERLA11DV3 | Heat pump |  | 30.8 | 7.08 | ERLA11-16DV3_Safety declaration of conformity_2P623915-3B.pdf | 2P623915-3B | EN 61000-3-12 | EN 61000-3-11 | 2256532.0501-EMC.pdf | 2256532.0501-EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.11109 | 0.476 | Requires Service Current Capacity ≥100A per phase | 0.354
[16 empty] | EBBX11D6V | Back-up heater - on-board |  | 8.7 | 2 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A.pdf | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2861 | Daikin | Altherma | ERLA11DV3 + EBBH11D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.8 | 7.08 | 30.8 | 7.08 | ERLA11DV3 | Heat pump |  | 30.8 | 7.08 | ERLA11-16DV3_Safety declaration of conformity_2P623915-3B.pdf | 2P623915-3B | EN 61000-3-12 | EN 61000-3-11 | 2256532.0501-EMC.pdf | 2256532.0501-EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.11109 | 0.476 | Requires Service Current Capacity ≥100A per phase | 0.354
[16 empty] | EBBH11D6V | Back-up heater - on-board |  | 8.7 | 2 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A.pdf | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2862 | Daikin | Altherma | ERLA14DV3 + EBBX16D6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.8 | 7.08 | 30.8 | 7.08 | ERLA14DV3 | Heat pump |  | 30.8 | 7.08 | ERLA11-16DV3_Safety declaration of conformity_2P623915-3B.pdf | 2P623915-3B | EN 61000-3-12 | EN 61000-3-11 | 2256532.0501-EMC.pdf | 2256532.0501-EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.11109 | 0.476 | Requires Service Current Capacity ≥100A per phase | 0.354
[16 empty] | EBBX16D6V | Back-up heater - on-board |  | 8.7 | 2 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A.pdf | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2863 | Daikin | Altherma | ERLA14DV3 + EBBH16D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.8 | 7.08 | 30.8 | 7.08 | ERLA14DV3 | Heat pump |  | 30.8 | 7.08 | ERLA11-16DV3_Safety declaration of conformity_2P623915-3B.pdf | 2P623915-3B | EN 61000-3-12 | EN 61000-3-11 | 2256532.0501-EMC.pdf | 2256532.0501-EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.11109 | 0.476 | Requires Service Current Capacity ≥100A per phase | 0.354
[16 empty] | EBBH16D6V | Back-up heater - on-board |  | 8.7 | 2 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A.pdf | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2864 | Daikin | Altherma | ERLA16DV37 + EBBX16D6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.8 | 7.08 | 30.8 | 7.08 | ERLA16DV3 | Heat pump |  | 30.8 | 7.08 | ERLA11-16DV3_Safety declaration of conformity_2P623915-3B.pdf | 2P623915-3B | EN 61000-3-12 | EN 61000-3-11 | 2256532.0501-EMC.pdf | 2256532.0501-EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.11109 | 0.476 | Requires Service Current Capacity ≥100A per phase | 0.354
[16 empty] | EBBX16D6V | Back-up heater - on-board |  | 8.7 | 2 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A.pdf | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2865 | Daikin | Altherma | ERLA16DV37 + EBBH16D6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.8 | 7.08 | 30.8 | 7.08 | ERLA16DV3 | Heat pump |  | 30.8 | 7.08 | ERLA11-16DV3_Safety declaration of conformity_2P623915-3B.pdf | 2P623915-3B | EN 61000-3-12 | EN 61000-3-11 | 2256532.0501-EMC.pdf | 2256532.0501-EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.11109 | 0.476 | Requires Service Current Capacity ≥100A per phase | 0.354
[16 empty] | EBBH16D6V | Back-up heater - on-board |  | 8.7 | 2 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A.pdf | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2866 | Daikin | Altherma | ERLA11DW1+EBBX11D9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | ERLA11DW1 | Heat pump |  | 14 | 9.7 | ERLA11-16DW1_Safety declaration of conformity_2P623915-4B | 2P623915-4B | EN 61000-3-2 | EN 61000-3-3 | 2256907.0501-EMC | 2256907.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EBBX11D9W | Back-up heater - on-board |  | 13 | 9 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 | 2256532.0501-EMC | 2256532.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2867 | Daikin | Altherma | ERLA11DW1+EBBH11D9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | ERLA11DW1 | Heat pump |  | 14 | 9.7 | ERLA11-16DW1_Safety declaration of conformity_2P623915-4B | 2P623915-4B | EN 61000-3-2 | EN 61000-3-3 | 2256907.0501-EMC | 2256907.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EBBH11D9W | Back-up heater - on-board |  | 13 | 9 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 | 2256532.0501-EMC | 2256532.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2868 | Daikin | Altherma | ERLA14DW1+EBBX16D9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | ERLA14DW1 | Heat pump |  | 14 | 9.7 | ERLA11-16DW1_Safety declaration of conformity_2P623915-4B | 2P623915-4B | EN 61000-3-2 | EN 61000-3-3 | 2256907.0501-EMC | 2256907.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EBBX16D9W | Back-up heater - on-board |  | 13 | 9 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 | 2256532.0501-EMC | 2256532.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2869 | Daikin | Altherma | ERLA14DW1+EBBH16D9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | ERLA14DW1 | Heat pump |  | 14 | 9.7 | ERLA11-16DW1_Safety declaration of conformity_2P623915-4B | 2P623915-4B | EN 61000-3-2 | EN 61000-3-3 | 2256907.0501-EMC | 2256907.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EBBH16D9W | Back-up heater - on-board |  | 13 | 9 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 | 2256532.0501-EMC | 2256532.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2870 | Daikin | Altherma | ERLA16DW17+EBBX16D9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | ERLA16DW1 | Heat pump |  | 14 | 9.7 | ERLA11-16DW1_Safety declaration of conformity_2P623915-4B | 2P623915-4B | EN 61000-3-2 | EN 61000-3-3 | 2256907.0501-EMC | 2256907.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EBBX16D9W | Back-up heater - on-board |  | 13 | 9 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 | 2256532.0501-EMC | 2256532.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2871 | Daikin | Altherma | ERLA16DW17+EBBH16D9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 14 | 9.7 | 14 | 9.7 | ERLA16DW1 | Heat pump |  | 14 | 9.7 | ERLA11-16DW1_Safety declaration of conformity_2P623915-4B | 2P623915-4B | EN 61000-3-2 | EN 61000-3-3 | 2256907.0501-EMC | 2256907.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | EBBH16D9W | Back-up heater - on-board |  | 13 | 9 | EBB(H-X)-D(6V-9W)_Safety declaration of conformity_3P663124-1A | 3P663124-1A | EN 61000-3-2 | EN 61000-3-3 | 2256532.0501-EMC | 2256532.0501-EMC | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2872 | Daikin | Altherma | EPGA11DV7+EABH16DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.061 | 30.7 | 7.061 | EPGA11DV7 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EABH16D6V7 | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2873 | Daikin | Altherma | EPGA11DV7+EABX16DA6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.061 | 30.7 | 7.061 | EPGA11DV7 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EABX16D6V7 | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2874 | Daikin | Altherma | EPGA14DV7+EABH16DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.061 | 30.7 | 7.061 | EPGA14DV7 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EABH16D6V7 | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2875 | Daikin | Altherma | EPGA14DV7+EABX16DA6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.061 | 30.7 | 7.061 | EPGA14DV7 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EABX16D6V7 | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2876 | Daikin | Altherma | EPGA16DV7+EABH16DA6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.061 | 30.7 | 7.061 | EPGA16DV7 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EABH16D6V7 | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2877 | Daikin | Altherma | EPGA16DV7+EABH16DA6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.061 | 30.7 | 7.061 | EPGA16DV7 | Heat pump |  | 30.7 | 7.06 | 10.EPGA11-16DAV3 - DoC14W900-2AE | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes | EPGA_2232577.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EABX16D6V7 | Back-up heater - on-board |  | 17.4 | 4 | 10.EABH16DA6V - DoC14W900-2AH.pdf | DoC14W900-2AH | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes |  |  |  |  | EPGA_2232577.0501-EMC | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2878 | Daikin | Altherma | EPGA11DAV7 + EAVH16SU18D6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.06 | 30.7 | 7.06 | EPGA11DAV7 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EAVH16SU18D6V7 | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2879 | Daikin | Altherma | EPGA11DAV7 + EAVH16SU23D6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.06 | 30.7 | 7.06 | EPGA11DAV7 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EAVH16SU23D6V7 | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2880 | Daikin | Altherma | EPGA14DAV7 + EAVH16SU18D6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.06 | 30.7 | 7.06 | EPGA14DAV7 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EAVH16SU18D6V7 | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2881 | Daikin | Altherma | EPGA14DAV7 + EAVH16SU23D6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.06 | 30.7 | 7.06 | EPGA14DAV7 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EAVH16SU23D6V7 | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2882 | Daikin | Altherma | EPGA16DAV7 + EAVH16SU18D6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.06 | 30.7 | 7.06 | EPGA16DAV7 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EAVH16SU18D6V7 | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2883 | Daikin | Altherma | EPGA16DAV7 + EAVH16SU23D6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.7 | 7.06 | 30.7 | 7.06 | EPGA16DAV7 | Heat pump |  | 30.7 | 7.061 | 10.EPGA11-16DAV3 - DoC14W900-2AE.pdf | DoC14W900-2AE | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1624 | 0.326 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | EAVH16SU23D6V7 | Back-up heater - on-board |  | 17.4 | 4.002 | DoC14W900-2AZ.pdf | DoC14W900-2AZ | EN 61000-3-12 | EN 61000-3-11 | EPGA_2232577.0501-EMC | 2232577.0501-EMC | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2884 | Daikin | Altherma | EPRA08EV3 + ETBH12E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA08EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETBH12E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2885 | Daikin | Altherma | EPRA08EV3 + ETBX12E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA08EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETBX12E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2886 | Daikin | Altherma | EPRA10EV3 + ETBH12E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA10EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETBH12E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2887 | Daikin | Altherma | EPRA10EV3 + ETBX12E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA10EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETBX12E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2888 | Daikin | Altherma | EPRA12EV3 + ETBH12E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA12EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETBH12E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2889 | Daikin | Altherma | EPRA12EV3 + ETBX12E6V | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA12EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETBX12E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2890 | Daikin | Altherma | EPRA08EV3+ETVH12SU18E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA08EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETVH12SU18E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2891 | Daikin | Altherma | EPRA08EV3+ETVH12SU23E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA08EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETVH12SU23E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2892 | Daikin | Altherma | EPRA10EV3+ETVH12SU18E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA10EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETVH12SU18E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2893 | Daikin | Altherma | EPRA10EV3+ETVH12SU23E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA10EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETVH12SU23E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2894 | Daikin | Altherma | EPRA12EV3+ETVH12SU18E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA12EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETVH12SU18E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2895 | Daikin | Altherma | EPRA12EV3+ETVH12SU23E6V | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.4 | 5.61 | 24.4 | 5.61 | EPRA12EV3 | Heat pump |  | 24.4 | 5.61 | DoC14W900-2BH.pdf | DoC14W900-2BH | EN 61000-3-12 | EN 61000-3-11 | TCF034B_(D4a)A1_2251400.0501-EMC.pdf | 2251400.0501-EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[16 empty] | ETVH12SU23E6V | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2896 | Daikin | Altherma | EPRA14DV37+ETBH16E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA14DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETBH16E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2897 | Daikin | Altherma | EPRA14DV37+ETBX16E6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA14DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETBX16E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2898 | Daikin | Altherma | EPRA16DV37+ETBH16E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA16DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETBH16E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2899 | Daikin | Altherma | EPRA16DV37+ETBX16E6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA16DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETBX16E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3501 | Daikin | Altherma | EPRA18DV37+ETBH16E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA18DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETBH16E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3502 | Daikin | Altherma | EPRA18DV37+ETBX16E6V7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA18DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETBX16E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BM | DoC14W900-2BM | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3503 | Daikin | Altherma | EPRA14DW17 + ETBH16E9W7 | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA14DW17 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBH16E9W7 | Back-up heater - on-board |  | 2.87 | 2 | DoC14W900-2AP_3PH_IU | DoC14W900-2AP | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3504 | Daikin | Altherma | EPRA14DW17 + ETBX16E9W7 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA14DW17 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBX16E9W7 | Back-up heater - on-board |  | 2.87 | 2 | DoC14W900-2AP_3PH_IU | DoC14W900-2AP | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3505 | Daikin | Altherma | EPRA16DW17 + ETBH16E9W7 | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA16DW17 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBH16E9W7 | Back-up heater - on-board |  | 2.87 | 2 | DoC14W900-2AP_3PH_IU | DoC14W900-2AP | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3506 | Daikin | Altherma | EPRA16DW17 + ETBX16E9W7 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA16DW17 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBX16E9W7 | Back-up heater - on-board |  | 2.87 | 2 | DoC14W900-2AP_3PH_IU | DoC14W900-2AP | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3507 | Daikin | Altherma | EPRA18DW17 + ETBH16E9W7 | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA18DW17 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBH16E9W7 | Back-up heater - on-board |  | 2.87 | 2 | DoC14W900-2AP_3PH_IU | DoC14W900-2AP | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3508 | Daikin | Altherma | EPRA18DW17 + ETBH16E9W7 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | EPRA18DW17 | Heat pump |  | 13 | 9 | DoC14W900-2AM_3PH_OU | DoC14W900-2AM | EN 61000-3-2 | EN 61000-3-3 | TCF034A_(D4d)A3 2237856.0501-EMC | 2237856.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBX16E9W7 | Back-up heater - on-board |  | 2.87 | 2 | DoC14W900-2AP_3PH_IU | DoC14W900-2AP | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3509 | Daikin | Altherma | EPRA14DV37+ETVH16SU18E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA14DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETVH16SU18E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3510 | Daikin | Altherma | EPRA14DV37+ETVH16SU23E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA14DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETVH16SU23E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3511 | Daikin | Altherma | EPRA16DV37+ETVH16SU18E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA16DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETVH16SU18E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3512 | Daikin | Altherma | EPRA16DV37+ETVH16SU23E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA16DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETVH16SU23E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3513 | Daikin | Altherma | EPRA18DV37+ETVH16SU18E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA18DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETVH16SU18E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3514 | Daikin | Altherma | EPRA18DV37+ETVH16SU23E6V7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | EPRA18DV37 | Heat pump |  | 22 | 5.06 | DoC14W900-2AL_1PH_OU | DoC14W900-2AL | EN 61000-3-12 | EN 61000-3-11 | TCF034A_(D4c)A3 2237855.0501-EMC | 2237855.0501-EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.1435 | 0.369 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | ETVH16SU23E6V7 | Back-up heater - on-board |  | 8.7 | 2 | DoC14W900-2BN | DoC14W900-2BN | EN 61000-3-2 | EN 61000-3-3 | [10 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3515 | Daikin | Altherma | EPRA08EW1+ETBH12E9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | EPRA08DW1 | Heat pump |  | 10 | 6.93 | DoC14W900-2BV.pdf | DoC14W900-2BV | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4d)B1_2258607.0501-EMC.pdf | 2258607.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBH12E9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3516 | Daikin | Altherma | EPRA08EW1+ETBX12E9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | EPRA08DW1 | Heat pump |  | 10 | 6.93 | DoC14W900-2BV.pdf | DoC14W900-2BV | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4d)B1_2258607.0501-EMC.pdf | 2258607.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBX12E9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3517 | Daikin | Altherma | EPRA10EW1+ETBH12E9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | EPRA10DW1 | Heat pump |  | 10 | 6.93 | DoC14W900-2BV.pdf | DoC14W900-2BV | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4d)B1_2258607.0501-EMC.pdf | 2258607.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBH12E9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3518 | Daikin | Altherma | EPRA10EW1+ETBX12E9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | EPRA10DW1 | Heat pump |  | 10 | 6.93 | DoC14W900-2BV.pdf | DoC14W900-2BV | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4d)B1_2258607.0501-EMC.pdf | 2258607.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBX12E9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3519 | Daikin | Altherma | EPRA12EW1+ETBH12E9W | Heating only | Air Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | EPRA12DW1 | Heat pump |  | 10 | 6.93 | DoC14W900-2BV.pdf | DoC14W900-2BV | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4d)B1_2258607.0501-EMC.pdf | 2258607.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBH12E9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3520 | Daikin | Altherma | EPRA12EW1+ETBX12E9W | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | EPRA12DW1 | Heat pump |  | 10 | 6.93 | DoC14W900-2BV.pdf | DoC14W900-2BV | EN 61000-3-2 | EN 61000-3-3 | TCF034B_(D4d)B1_2258607.0501-EMC.pdf | 2258607.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | ETBX12E9W | Back-up heater - on-board |  | 2.9 | 2 | DoC14W900-2BJ.pdf | DoC14W900-2BJ | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3521 | Daikin | Altherma | EBLA04EV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.9 | 4.58 | 19.9 | 4.58 | EBLA04EV3 | Heat pump |  | 19.9 | 4.57 | 3P685234-5B_EB_DLA04_08E_web_Turkey | 3P685234-5B | EN 61000-3-12 | EN 61000-3-11 | 80119473-00.pdf | 80119473-00 Rev_0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3522 | Daikin | Altherma | EBLA06EV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.9 | 4.58 | 19.9 | 4.58 | EBLA06EV3 | Heat pump |  | 19.9 | 4.57 | 3P685234-5B_EB_DLA04_08E_web_Turkey | 3P685234-5B | EN 61000-3-12 | EN 61000-3-11 | 80119473-00.pdf | 80119473-00 Rev_0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3523 | Daikin | Altherma | EBLA08EV3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24 | 5.52 | 24 | 5.52 | EBLA08EV3 | Heat pump |  | 24 | 5.52 | 3P685234-5B_EB_DLA04_08E_web_Turkey | 3P685234-5B | EN 61000-3-12 | EN 61000-3-11 | 80119473-00.pdf | 80119473-00 Rev_0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3524 | Daikin | Altherma | EDLA04EV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 19.9 | 4.58 | 19.9 | 4.58 | EDLA04EV3 | Heat pump |  | 19.9 | 4.57 | 3P685234-5B_EB_DLA04_08E_web_Turkey | 3P685234-5B | EN 61000-3-12 | EN 61000-3-11 | 80119473-00.pdf | 80119473-00 Rev_0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3525 | Daikin | Altherma | EDLA06EV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 19.9 | 4.58 | 19.9 | 4.58 | EDLA06EV3 | Heat pump |  | 19.9 | 4.57 | 3P685234-5B_EB_DLA04_08E_web_Turkey | 3P685234-5B | EN 61000-3-12 | EN 61000-3-11 | 80119473-00.pdf | 80119473-00 Rev_0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3526 | Daikin | Altherma | EDLA08EV3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 24 | 5.52 | 24 | 5.52 | EDLA08EV3 | Heat pump |  | 24 | 5.52 | 3P685234-5B_EB_DLA04_08E_web_Turkey | 3P685234-5B | EN 61000-3-12 | EN 61000-3-11 | 80119473-00.pdf | 80119473-00 Rev_0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3527 | Daikin | Altherma | EWSAH06UDA9W | Heating only | Water Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | EWSAH06UDA9W | Heat pump |  | 26 | 5.98 | EWSA(H-X)-UD9W_Safety declaration of conformity_3P570461-4C | 3P570461-4C | EN 61000-3-12 | EN 61000-3-11 | testreport part | TRF_EMC-GEN R2.0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3528 | Daikin | Altherma | EWSAX06UDA9W | Heating & Cooling | Water Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | EWSAX06UDA9W | Heat pump |  | 26 | 5.98 | EWSA(H-X)-UD9W_Safety declaration of conformity_3P570461-4C | 3P570461-4C | EN 61000-3-12 | EN 61000-3-11 | testreport part | TRF_EMC-GEN R2.0 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3529 | Daikin | Altherma | EBLQ011CAW1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EBLQ011CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 4.33 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3530 | Daikin | Altherma | EBLQ014CAW1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EBLQ014CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 4.33 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3531 | Daikin | Altherma | EBLQ016CAW1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EBLQ016CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 4.33 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3532 | Daikin | Altherma | EDLQ011CAW1 | Heating Only | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EDLQ011CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 4.33 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3533 | Daikin | Altherma | EDLQ014CAW1 | Heating Only | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EDLQ014CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 4.33 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3534 | Daikin | Altherma | EDLQ016CAW1 | Heating Only | Air Source | 3 | 400 |  |  |  |  | 16.3 | 11.29 | 16.3 | 11.29 | EDLQ016CAW1 | Heat pump |  | 16.3 | 11.25 | C Series GQI Monobloc - 3Phase DoC | 14DoC14W900-1ZV | EN 61000-3-12 | EN 61000-3-11 | 2225822.0501-EMC | 2225822.0501-EMC | Yes | No | No | No | Yes | No | Yes | 2225822.0501-EMC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 4.33 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0101 | Dimplex | LA12MI | LA12MI | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 64 | 14.72 | 64 | 14.72 | LA12MI | Heat pump |  | 25 | 5.52 | [8 empty] | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 858 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater |  | 26 | 6 | [8 empty] | No |  |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.236
[17 empty] | Boost heater |  | 13 | 3 | [8 empty] | No |  |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.464
HP_0201 | LG | HM161M.U33 | HM161M.U33 | Heating only | Air Source | 1 | 230 |  |  |  |  | 16.763 | 3.855 | 42 | 9.66 | HM161M.U33 | Whole system |  | 16.763 | 3.85 | E_DMZ_HM161M_DOC_20180907000006 | 01 202 ROK/Ü-133048767-25 | EN 61000-3-12 | EN 61000-3-11 | Heat pumps(ZHBW166A0)_CB_Report_attachment | 077-2137818-000 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes
HP_0202 | LG | HM091M.U43 | HM091M.U43 | Heating only | Air Source | 1 | 230 |  |  |  |  | 7 | 1.61 | 27.6 | 6.34 | HM091M.U43 | Whole system |  | 7 | 1,61 | E_DMZ_HM091M_DOC_20180907000007 | 01 202 ROK/Ü-133048767-27 | EN 61000-3-12 | EN 61000-3-11 | Heat Pumps(ZHBW096A0)_Report_attachment1_Rev | 077-2210218-000 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes
HP_0203 | LG | HM141M.U33 | HM141M.U33 | Heating only | Air Source | 1 | 230 |  |  |  |  | 16.763 | 3.855 | 42 | 9.66 | HM141M.U33 | Whole system |  | 16.763 | 3.85 | E_DMZ_HM141M_DOC_20180907000006 | 01 202 ROK/Ü-133048767-25 | EN 61000-3-12 | EN 61000-3-11 | Heat pumps(ZHBW166A0)_CB_Report_attachment | 077-2137818-000 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes
HP_0204 | LG | HM051M.U43 | HM051M.U43 | Heating only | Air Source | 1 | 230 |  |  |  |  | 7 | 1.61 | 27.6 | 6.34 | HM051M.U43 | Whole system |  | 7 | 1.61 | E_DMZ_HM051M_DOC_20180907000007 | 01 202 ROK/Ü-133048767-27 | EN 61000-3-12 | EN 61000-3-11 | Heat Pumps(ZHBW096A0)_Report_attachment1_Rev | 077-2210218-000 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes
HP_0205 | LG | HM071M.U43 | HM071M.U43 | Heating only | Air Source | 1 | 230 |  |  |  |  | 7 | 1.61 | 27.6 | 6.34 | HM071M.U43 | Whole system |  | 7 | 1.61 | E_DMZ_HM071M_DOC_20180907000007 | 01 202 ROK/Ü-133048767-27 | EN 61000-3-12 | EN 61000-3-11 | Heat Pumps(ZHBW096A0)_Report_attachment1_Rev | 077-2210218-000 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes
HP_0206 | LG | HM121M.U33 | HM121M.U33 | Heating only | Air Source | 1 | 230 |  |  |  |  | 16.763 | 3.855 | 42 | 9.66 | HM121M.U33 | Whole system |  | 16.763 | 3.85 | E_DMZ_HM121M_DOC_20180907000006 | 01 202 ROK/Ü-133048767-25 | EN 61000-3-12 | EN 61000-3-11 | Heat pumps(ZHBW166A0)_CB_Report_attachment | 077-2137818-000 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes
HP_0207 | LG | Therma V | HN1610H.NK2, HU161H.U32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 30.3 | 6.97 | 39 | 8.97 | HN1610H.NK2 | Heat pump |  | 15.9 | 3.66 | E_DMZ_HN1610H_DOC_20190528000005 + P28 Stage 2 Assessment | E_DMZ_HN1610H_DOC_20190528000005 + P28 Stage 2 Assessment | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report [Reg.No.50261143 0001] Therma-V 16.0 kW HT Split + P28 Stage 2 Assessment | EMC Test Report [Reg.No.50261143 0001] Therma-V 16.0 kW HT Split + P28 Stage 2 Assessment | No | No | No | No | No | No | Yes | LG Therma V Heat Pump Summary v1 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.177
[16 empty] | HU161H.U32 | Heat pump |  | 14.4 | 3.31 | E_DMZ_HU161H_DOC_20161207000010 + P28 Stage 2 Assessment | E_DMZ_HU161H_DOC_20161207000010 + P28 Stage 2 Assessment | EN 61000-3-12 | EN 61000-3-11 | [5 empty] | No |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_0208 | LG | Therma V LV Splits | HU051MR U44 + HN0916M NK4 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.69 | 12.35 | 53.69 | 12.35 | HU051MR U44 + HN0916M NK4 | Heat pump |  | 27.6 | 6.35 | E_DMZ_HU051MR_DOC_20191008000015 | E_DMZ_HU051MR_DOC_20191008000015 | EN 61000-3-12 | EN 61000-3-11 | HU051MR,HU071MR,HU091MR,HN0916M_AE 50430787 0001_50228759 001 | 50228759 001 | Yes | No | No | No | No | No | Yes | 50228759 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 26.09 | 6 | E_DMZ_HN0916M_DOC_20191008000019 | E_DMZ_HN0916M_DOC_20191008000019 | EN 61000-3-12 | EN 61000-3-11 | HU051MR,HU071MR,HU091MR,HN0916M_AE 50430787 0001_50228759 001 | 50228759 001 | No | No | No | No | No | No | Yes | 50228759 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
HP_0209 | LG | Therma V LV Splits | HU071MR U44 + HN0916M NK4 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.69 | 12.35 | 53.69 | 12.35 | HU071MR U44 + HN0916M NK4 | Heat pump |  | 27.6 | 6.35 | E_DMZ_HU071MR_DOC_20191008000014 | E_DMZ_HU071MR_DOC_20191008000014 | EN 61000-3-12 | EN 61000-3-11 | HU051MR,HU071MR,HU091MR,HN0916M_AE 50430787 0001_50228759 001 | 50228759 001 | Yes | No | No | No | No | No | Yes | 50228759 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 26.09 | 6 | E_DMZ_HN0916M_DOC_20191008000019 | E_DMZ_HN0916M_DOC_20191008000019 | EN 61000-3-12 | EN 61000-3-11 | HU051MR,HU071MR,HU091MR,HN0916M_AE 50430787 0001_50228759 001 | 50228759 001 | No | No | No | No | No | No | Yes | 50228759 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
HP_0210 | LG | Therma V LV Splits | HU091MR U44 + HN0916M NK4 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.69 | 12.35 | 53.69 | 12.35 | HU091MR U44 + HN0916M NK4 | Heat pump |  | 27.6 | 6.35 | E_DMZ_HU091MR_DOC_20191008000011 | E_DMZ_HU091MR_DOC_20191008000011 | EN 61000-3-12 | EN 61000-3-11 | HU051MR,HU071MR,HU091MR,HN0916M_AE 50430787 0001_50228759 001 | 50228759 001 | Yes | No | No | No | No | No | Yes | 50228759 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | HU091MR U44 + HN0916M NK4 | Back-up heater - on-board |  | 26.09 | 6 | E_DMZ_HN0916M_DOC_20191008000019 | E_DMZ_HN0916M_DOC_20191008000019 | EN 61000-3-12 | EN 61000-3-11 | HU051MR,HU071MR,HU091MR,HN0916M_AE 50430787 0001_50228759 001 | 50228759 001 | No | No | No | No | No | No | Yes | 50228759 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
HP_0211 | LG | Therma V | HU161HA.U33, HN1610H.NK3 | Heating only | Air Source | 1 | 230 |  |  |  |  | 27 | 6.21 | 39.1 | 8.99 | HU161HA U33 | Heat pump |  | 18.9 | 4.35 | AH-W166T3_AE 50437622 0001_50230050 002 | 50230050 002 | EN 61000-3-12 | EN 61000-3-11 | AH-W166T3_AE 50437622 0001_50230050 001 | 50230050 001 | Yes | No | No | No | No | No | Yes | AH-W166T3_AE 50437622 0001_50230050 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
[16 empty] | HN1610H NK3 | Heat pump |  | 20.2 | 4.65 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354 | No |  |  | No |  |  | No
HP_0212 | LG | Therma V LV Splits | HU121 U33 + HN1616 NK3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 51.08 | 11.75 | 51..08 | 11.75 | HU121 U33 | Heat pump |  | 25 | 5.75 | AHNW16606A3(AHUW166A3)CERT_CB.pdf | SG PSB-EC-00406 | EN 61000-3-12 | EN 61000-3-11 | AHNW16606A3(AHUW166A3)_attachment1_CB.pdf, AHNW16606A3(AHUW166A3)_attachment2_CB.pdf | 077-2101019-000 | No | Yes | No | No | No | No | Yes | 077-2101019-000 | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.0866 | 0.611 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | HN1616 NK3 | Back-up heater - on-board |  | 26.08 | 6 | AHNW16606A3(AHUW166A3)CERT_CB.pdf | SG PSB-EC-00406 | EN 61000-3-12 | EN 61000-3-11 | AHNW16606A3(AHUW166A3)_attachment1_CB.pdf, AHNW16606A3(AHUW166A3)_attachment2_CB.pdf | 077-2101019-000 | Yes | No | No |  |  |  |  | 077-2101019-000 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2166 | No |  |  | No |  |  | No
HP_0213 | LG | Therma V LV Splits | HU141 U33 + HN1616 NK3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 51.08 | 11.75 | 51..08 | 11.75 | HU141 U33 | Heat pump |  | 25 | 5.75 | AHNW16606A3(AHUW166A3)CERT_CB.pdf | SG PSB-EC-00406 | EN 61000-3-12 | EN 61000-3-11 | AHNW16606A3(AHUW166A3)_attachment1_CB.pdf, AHNW16606A3(AHUW166A3)_attachment2_CB.pdf | 077-2101019-000 | No | Yes | No | No | No | No | Yes | 077-2101019-000 | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.0866 | 0.611 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | HN1616 NK3 | Back-up heater - on-board |  | 26.08 | 6 | AHNW16606A3(AHUW166A3)CERT_CB.pdf | SG PSB-EC-00406 | EN 61000-3-12 | EN 61000-3-11 | AHNW16606A3(AHUW166A3)_attachment1_CB.pdf, AHNW16606A3(AHUW166A3)_attachment2_CB.pdf | 077-2101019-000 | Yes | No | No |  |  |  |  | 077-2101019-000 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2166 | No |  |  | No |  |  | No
HP_0214 | LG | Therma V LV Splits | HU161 U33 + HN1616 NK3 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 51.08 | 11.75 | 51..08 | 11.75 | HU161 U33 | Heat pump |  | 25 | 5.75 | AHNW16606A3(AHUW166A3)CERT_CB.pdf | SG PSB-EC-00406 | EN 61000-3-12 | EN 61000-3-11 | AHNW16606A3(AHUW166A3)_attachment1_CB.pdf, AHNW16606A3(AHUW166A3)_attachment2_CB.pdf | 077-2101019-000 | No | Yes | No | No | No | No | Yes | 077-2101019-000 | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.0866 | 0.611 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | HN1616 NK3 | Back-up heater - on-board |  | 26.08 | 6 | AHNW16606A3(AHUW166A3)CERT_CB.pdf | SG PSB-EC-00406 | EN 61000-3-12 | EN 61000-3-11 | AHNW16606A3(AHUW166A3)_attachment1_CB.pdf, AHNW16606A3(AHUW166A3)_attachment2_CB.pdf | 077-2101019-000 | Yes | No | No |  |  |  |  | 077-2101019-000 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2166 | No |  |  | No |  |  | No
HP_0215 | LG | 5 kW R32 Monoblock (Gen.2) | HM051MR.U44 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.2 | 3.27 | 14.2 | 3.27 | HM051MR.U44 | Whole system |  | 14.2 | 3.27 | ZHBW096A1_CPSC01271021CERT_CE |  | EN 61000-3-2 | EN 61000-3-3 | ZHBW096A1_CPSC01271021TRF_CE | CPSC01271021 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0216 | LG | 7 kW R32 Monoblock (Gen.2) | HM071MR.U44 | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.61 | 15.7 | 3.61 | HM071MR.U44 | Whole system |  | 15.7 | 3.61 | ZHBW096A1_CPSC01271021CERT_CE |  | EN 61000-3-2 | EN 61000-3-3 | ZHBW096A1_CPSC01271021TRF_CE | CPSC01271021 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0217 | LG | 9 kW R32 Monoblock (Gen.2) | HM091MR.U44 | Heating only | Air Source | 1 | 230 |  |  |  |  | 23 | 5.29 | 23 | 5.29 | HM091MR.U44 | Whole system |  | 23 | 5.29 | ZHBW096A1_CPSC01271021CERT_CE |  | EN 61000-3-12 | EN 61000-3-11 | ZHBW096A1_CPSC01271021TRF_CE | CPSC01271021 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0218 | LG | 12 kW 1-phase R32 Monoblock (Gen.2) | HM121MR.U34 | Heating Only | Air Source | 1 | 230 |  |  |  |  | 35 | 8.05 | 35 | 8.05 | HM121MR.U34 | Heat pump |  | 35 | 8 | ZHBW166A1_EMC Certi_AK 50511198 0001-0002 | KR21A212 001 | EN 61000-3-12 | EN 61000-3-11 | ZHBW166A1_EMC Report_KR21A212 001 | KR21A212 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.094 | 0.5629 | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0219 | LG | 14 kW 1-phase R32 Monoblock (Gen.2) | HM141MR.U34 | Heating Only | Air Source | 1 | 230 |  |  |  |  | 35 | 8.05 | 35 | 8.05 | HM141MR.U34 | Heat pump |  | 35 | 8 | ZHBW166A1_EMC Certi_AK 50511198 0001-0002 | KR21A212 001 | EN 61000-3-12 | EN 61000-3-11 | ZHBW166A1_EMC Report_KR21A212 001 | KR21A212 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.094 | 0.5629 | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0220 | LG | 16 kW 1-phase R32 Monoblock (Gen.2) | HM161MR.U34 | Heating Only | Air Source | 1 | 230 |  |  |  |  | 35 | 8.05 | 35 | 8.05 | HM161MR.U34 | Heat pump |  | 35 | 8 | ZHBW166A1_EMC Certi_AK 50511198 0001-0002 | KR21A212 001 | EN 61000-3-12 | EN 61000-3-11 | ZHBW166A1_EMC Report_KR21A212 001 | KR21A212 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.094 | 0.5629 | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0221 | LG | 12 kW 3-phase R32 Monoblock (Gen.2) | HM123MR.U34 | Heating Only | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | HM123MR.U34 | Heat pump |  | 16.1 | 11.15 | ZHBW168A1_AK 50512664 0001-0002 | AK 50512664 0001-0002 | EN 61000-3-12 | EN 61000-3-3 | ZHBW168A1_KR21X327 001 | KR21X327 001 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2672 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0222 | LG | 14 kW 3-phase R32 Monoblock (Gen.2) | HM143MR.U34 | Heating Only | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | HM143MR.U34 | Heat pump |  | 16.1 | 11.15 | ZHBW168A1_AK 50512664 0001-0002 | AK 50512664 0001-0002 | EN 61000-3-12 | EN 61000-3-3 | ZHBW168A1_KR21X327 001 | KR21X327 001 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2672 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0223 | LG | 16 kW 3-phase R32 Monoblock (Gen.2) | HM163MR.U34 | Heating Only | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | HM163MR.U34 | Heat pump |  | 16.1 | 11.15 | ZHBW168A1_AK 50512664 0001-0002 | AK 50512664 0001-0002 | EN 61000-3-12 | EN 61000-3-3 | ZHBW168A1_KR21X327 001 | KR21X327 001 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2672 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0302 | Kensa | Shoebox 3kW | S3-P0K | Heating only | Ground Source | 1 | 230 |  |  |  |  | 7 | 1.61 | 7 | 1.61 | S3-P0K | Heat pump |  | 7 | 1.61 | Kensa.S3-P0K.DoC.pdf | Kensa.S3-P0K.DoC.pdf | EN 61000-3-2 | EN 61000-3-3 | C28545 EMC Test Report 01 | C28545 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0303 | Kensa | Evo 13kW | K130-S1H | Heating only | Ground Source | 1 | 230 |  |  |  |  | 31.1 | 7.15 | 31.1 | 7.15 | K130-S1H | Heat pump |  | 31.1 | 7.15 | Evo 13kW DofC.pdf | Evo 13kW DofC.pdf | EN 61000-3-12 | EN 61000-3-11 | Evo 13 EMC Test Report final.pdf | 5914 | Yes | Yes | Yes | Yes | Yes | Yes | No | Evo 13kW DofC.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0304 | Kensa | Evo 7kW | K070-S1H | Heating only | Ground Source | 1 | 230 |  |  |  |  | 17.4 | 4 | 17.4 | 4 | K070-S1H | Heat pump |  | 17.4 | 4 | Evo 7kW DofC.pdf | Evo 7kW DofC.pdf | EN 61000-3-12 | EN 61000-3-11 | Evo 7 EMC Test Report.pdf + Evo 7 Flicker Data.pdf + Evo 7 Harmonics Data.pdf | E4582 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0305 | Kensa | Shoebox 6kW | S6-P0K | Heating only | Ground Source | 1 | 230 |  |  |  |  | 14 | 3.22 | 14 | 3.22 | S6-P0K | Heat pump |  | 14 | 3.22 | Kensa.S6-POK.DOC | Kensa.S6-POK.DOC | EN 61000-3-2 | EN 61000-3-3 | Shoebox 6 EMC test + Shoebox 6 flicker with stop-start V2 | Shoebox 6 EMC test + Shoebox 6 flicker with stop-start V2 | Yes | Yes | Yes | Yes | Yes | Yes | No | Shoebox 6 EMC test + Shoebox 6 flicker with stop-start V2 | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0306 | Kensa | Evo 9kW | K090-S1H | Heating only | Ground Source | 1 | 230 |  |  |  |  | 21.8 | 5.01 | 21.8 | 5.01 | K090-S1H | Heat pump |  | 21.8 | 5.01 | Evo 9kW DofC.pdf | Evo 9kW DofC.pdf | EN 61000-3-12 | EN 61000-3-11 | Evo 9kW Harmonics Flicker Test Final.pdf | 5908 | Yes | Yes | Yes | Yes | Yes | Yes | No | Evo 9kW DofC.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0307 | Kensa | Evo 15kW | K150-S3H | Heating only | Ground Source | 3 | 400 |  |  |  |  | 12 | 8.31 | 12 | 8.31 | K150-S3H | Heat pump |  | 12 | 8.28 | Evo 15 DofC.pdf | Evo 15 DofC.pdf | EN 61000-3-2 | EN 61000-3-3 | Evo 15 EMC Test Report.pdf | 5830 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0308 | Kensa | Evo 17kW | K170-S1H | Heating only | Ground Source | 1 | 230 |  |  |  |  | 37 | 8.51 | 37 | 8.51 | K170-S1H | Heat pump |  | 37 | 8.51 | Evo 17kW DofC.pdf | Evo 17kW DofC.pdf | EN 61000-3-12 | EN 61000-3-11 | Evo 17 EMC Test Report.pdf | 5791 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_0309 | Kensa | Kensa Q | Q80 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 64 | 44.34 | 64 | 44.34 | Q80 | Heat pump |  | 64 | 44.34 | UK Declaration of Conformity Commercial range v2 |  | EN 61000-3-12 | EN 61000-3-11 | Kensa HP Q80 PQ Assessment v2_Issued | 100421 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.0849
HP_0501 | MasterTherm | AquaMaster Inverter | AQ30i1 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | AQ30i1 | Heat pump |  | 18 | 4.14 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.09522 | 0.556 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0502 | MasterTherm | AquaMaster Inverter | AQ60i | Heating only | Ground Source | 3 | 400 |  |  |  |  | 24 | 16.63 | 24 | 16.63 | AQ60i | Heat pump |  | 24 | 16.6 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | No | Yes | No | No | Yes | No | Yes | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1496 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0503 | MasterTherm | BoxAir Inverter | BA37i1 | Heating only | Air Source | 1 | 230 |  |  | 19.26 |  | 26 | 5.98 | 26 | 5.98 | BA37i1 | Heat pump |  | 32 | 7.36 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 29 | 0.213 | 0.248 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0504 | MasterTherm | AquaMaster Inverter | AQ37i1 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | AQ37i1 | Heat pump |  | 32 | 7.36 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.206 | 0.257 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0505 | MasterTherm | AquaMaster Inverter | AQ17i1 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | AQ17i1 | Whole system |  | 16 | 3.68 | emc_eng_062019.pdf | emc_eng_062019.pdf | EN 61000-3-2 | EN 61000-3-3 | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | AQ22I1_harmonics_02032020 + AQ45I1_flicker_19022020.pdf | Yes | Yes | Yes | Yes | Yes | Yes | No | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0506 | MasterTherm | AquaMaster Inverter | AQ22i1 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | AQ22I1 | Whole system |  | 16 | 3.68 | emc_eng_062019.pdf | emc_eng_062019.pdf | EN 61000-3-2 | EN 61000-3-3 | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | AQ22I1_harmonics_02032020 + AQ45I1_flicker_19022020 | Yes | Yes | Yes | Yes | Yes | Yes | No | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0507 | MasterTherm | BoxAir Inverter | BA22i1 | Heating only | Air Source | 1 | 230 |  |  | 8.42 |  | 16 | 3.68 | 16 | 3.68 | BA22I1 | Whole system |  | 16 | 3.68 | emc_eng_062019.pdf | emc_eng_062019.pdf | EN 61000-3-2 | EN 61000-3-3 | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | AQ22I1_harmonics_02032020 + AQ45I1_flicker_19022020 | Yes | Yes | Yes | Yes | Yes | Yes | No | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0508 | MasterTherm | BoxAir Inverter | BA45i1 | Heating only | Air Source | 1 | 230 |  |  | 20.96 |  | 31 | 7.13 | 31 | 7.13 | BA45i1 | Heat pump |  | 31 | 7.1 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-3 | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | Equipment complying with IEC 61000-3-12 |  |  | 24 | 0.177 | 0.299 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0509 | MasterTherm | AquaMaster Inverter | AQ45i1 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 31 | 7.13 | 31 | 7.13 | AQ45i1 | Heat pump |  | 31 | 7.1 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-3 | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | Equipment complying with IEC 61000-3-12 |  |  | 24 | 0.177 | 0.299 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0510 | MasterTherm | AquaMaster Inverter | AQ26i1 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | AQ26i1 | Heat pump |  | 18 | 4.14 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.09522 | 0.556 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0511 | Mastertherm | AquaMaster Inverter | AQ37i | Heating only | Ground Source | 3 | 400 |  |  |  |  | 12 | 8.31 | 12 | 8.31 | AQ37i | Heat pump |  | 12 | 8.3 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 748 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0512 | Mastertherm | AquaMaster Inverter | AQ45i | Heating only | Ground Source | 3 | 400 |  |  |  |  | 12 | 8.31 | 12 | 8.31 | AQ45i | Heat pump |  | 12 | 8.3 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 748 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0513 | Mastertherm | AquaMaster Inverter | AQ90i | Heating only | Ground Source | 3 | 400 |  |  |  |  | 28 | 19.4 | 28 | 19.4 | AQ90i | Heat pump |  | 28 | 19 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032021.pdf | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032021.pdf | No | Yes | No | No | Yes | No | Yes | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032021.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1746 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0514 | Mastertherm | BoxAir Inverter | BA26i1 | Heating only | Air Source | 1 | 230 |  |  | 13.46 |  | 18 | 4.14 | 18 | 4.14 | BA26i1 | Heat pump |  | 18 | 4.14 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.09522 | 0.556 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0515 | Mastertherm | BoxAir Inverter | BA30i1 | Heating only | Air Source | 1 | 230 |  |  | 13.58 |  | 18 | 4.14 | 18 | 4.14 | BA30i1 | Heat pump |  | 18 | 4.14 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.09522 | 0.556 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0516 | Mastertherm | BoxAir Inverter | BA37i | Heating only | Air Source | 3 | 400 | 8.1 |  |  |  | 12 | 8.31 | 12 | 8.31 | BA37i | Heat pump |  | 12 | 8.3 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 748 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0517 | Mastertherm | BoxAir Inverter | BA45i | Heating only | Air Source | 3 | 400 |  |  | 8.4 |  | 12 | 8.31 | 12 | 8.31 | BA45i | Heat pump |  | 12 | 8.3 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 748 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0518 | Mastertherm | BoxAir Inverter | BA60i | Heating only | Air Source | 3 | 400 |  |  | 15.1 |  | 24 | 16.63 | 24 | 16.63 | BA60i | Heat pump |  | 24 | 16.6 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | No | Yes | No | No | Yes | No | Yes | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1496 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0519 | MasterTherm | BoxAir Inverter | BA37i1 | Heating only | Air Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | BA37i1 | Heat pump |  | 32 | 7.36 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA37I1_harmonics_02032021.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 29 | 0.213 | 0.248 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0520 | MasterTherm | BoxAir Inverter | BA22i1 | Heating only | Air Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | BA22I1 | Heat pump |  | 16 | 3.68 | emc_eng_062019.pdf | emc_eng_062019.pdf | EN 61000-3-2 | EN 61000-3-3 | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | AQ22I1_harmonics_02032020 + AQ45I1_flicker_19022020 | Yes | Yes | Yes | Yes | Yes | Yes | No | AQ22I1_harmonics_02032020.pdf + AQ45I1_flicker_19022020.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0521 | MasterTherm | BoxAir Inverter | BA45i1 | Heating only | Air Source | 1 | 230 |  |  |  |  | 31 | 7.13 | 31 | 7.13 | BA45i1 | Heat pump |  | 31 | 7.1 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-3 | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I1_harmonics_02032021.pdf + AQ45I1_flicker_19022021_rev1.pdf | Equipment complying with IEC 61000-3-12 |  |  | 24 | 0.177 | 0.299 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 26 | 5.98 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.246
HP_0522 | Mastertherm | BoxAir Inverter | BA26i1 | Heating only | Air Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | BA26i1 | Heat pump |  | 18 | 4.14 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.09522 | 0.556 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0523 | Mastertherm | BoxAir Inverter | BA30i1 | Heating only | Air Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | BA30i1 | Heat pump |  | 18 | 4.14 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | No | Yes | No | No | Yes | No | Yes | BA26I_harmonics_21122020.pdf + BA37IS1_flicker_05022020.pdf | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.09522 | 0.556 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0524 | Mastertherm | BoxAir Inverter | BA37i | Heating only | Air Source | 3 | 400 |  |  |  |  | 12 | 8.31 | 12 | 8.31 | BA37i | Heat pump |  | 12 | 8.3 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 748 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 4.33 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0525 | Mastertherm | BoxAir Inverter | BA45i | Heating only | Air Source | 3 | 400 |  |  |  |  | 12 | 8.31 | 12 | 8.31 | BA45i | Heat pump |  | 12 | 8.3 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | No | Yes | No | No | Yes | No | Yes | AQ45I_harmonics_01022021.pdf + AQ45I_flicker_01022021.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 748 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 8.66 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [8 empty] | N/A | N/A | N/A | Not applicable
HP_0526 | Mastertherm | BoxAir Inverter | BA60i | Heating only | Air Source | 3 | 400 |  |  |  |  | 24 | 16.63 | 24 | 16.63 | BA60i | Heat pump |  | 24 | 16.6 | E673_PROHOSHODE_emc_eng_09032021.pdf | E673_PROHOSHODE_emc_eng_09032021 | EN 61000-3-12 | EN 61000-3-11 | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | No | Yes | No | No | Yes | No | Yes | AQ90I_harmonics_02032021.pdf + AQ90I_flicker_09032020.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1496 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0601 | Mitsubishi Electric | Ecodan | PUHZ-W50VHA(-BS) | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PUHZ-W50VHA(-BS) | Whole system |  | 13 | 3.05 | Mitsubishi Ecodan 5kW Conformity Document.pdf | CE2013A24 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Carey Close, Moulton - New Form A - PUHZ W50VHA-BS.doc |  |  |  | N/A | N/A | N/A
HP_0602 | Mitsubishi Electric | Ecodan | PUHZ-W85VAA(-BS) | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | PUHZ-W85VAA(-BS) | Whole system |  | 22 | 5.06 | 180717_DOC_PUHZ-W60_85_SW75.pdf | CE2018C03 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Form A PUHZ W60 85.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A
HP_0603 | Mitsubishi Electric | Ecodan | PUHZ-W85VHA2(-BS) | Heating only | Air Source | 1 | 230 |  |  |  |  | 23 | 5.29 | 23 | 5.29 | PUHZ-W85VHA2(-BS) | Whole system |  | 23 | 5.29 | DoC Ecodan_PUHZ-W85VHA2-BS.pdf | CE2013C10 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Form J1 - PUHZ-W85VHA2-BS.doc | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A
HP_0604 | Mitsubishi Electric | Ecodan | PUHZ-W112VAA(-BS) | Heating only | Air Source | 1 | 230 |  |  |  |  | 28 | 6.44 | 28 | 6.44 | PUHZ-W112VAA(-BS) | Whole system |  | 28 | 6.44 | 11.2kw DECLARATION OF CONFORMITY.PDF | CE2018C04 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | New Form B PUHZ-W112VAA.DOC | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0605 | Mitsubishi Electric | Ecodan | PUHZ-HW140VHA(-BS) | Heating only | Air Source | 1 | 230 |  |  |  |  | 35.7 | 8.21 | 35.7 | 8.21 | PUHZ-W140VHA(-BS) | Whole system |  | 35.7 | 8.21 | DoC_for_PUHW HW140VHA2-BS.pdf | CE2016A37 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | No | No | Yes | Form A - PUHZ HW140VHA2-BS.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A
HP_0606 | Mitsubishi Electric | Ecodan | QUHZ-W40VA + EHPT20Q | Heating only | Air Source | 1 | 230 |  |  |  |  | 12 | 2.76 | 21.5 | 4.94 | QUHZ-W40VA + EHPT20Q | Whole system |  | 12 | 2.76 | DoC_QUHZ-W40VA + DoC_EHPT20Q-VM2EA | GCE201502-C + GCE201501-C | EN 61000-3-2 | EN 61000-3-3 | EMC test report1_EHPT20Q-VM2EA | T1560201 | Yes | Yes | Yes | Yes | Yes | Yes | No | Databook_QUHZ-W40VA+EHPT20Q.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable | [7 empty] | Yes | No
HP_0607 | Mitsubishi Electric | Ecodan | PUZ-WM50VHA | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PUZ-WM50VHA | Heat pump | PUZ-WM50VHA.UK 0A00001 | 13 | 2.99 | DoC_PUZ-WM50VHA.pdf | CE2020C11 | EN 61000-3-2 | EN 61000-3-3 | TR19E6211.pdf | TR19E6211 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM50VHA Databook | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0608 | Mitsubishi Electric | Ecodan | PUHZ-ZRP200YKA | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21 | 14.55 | 21 | 14.55 | PUHZ-ZRP200YKA | Heat pump |  | 21 | 14.55 | PUHZ-ZRP200250_Declaration_of_Conformity__CE2014C18_ | CE2014C18 | EN 61000-3-12 | EN 61000-3-11 | TR14E5211 | TR14E5211_PUHZ-ZRP200250YKA | No | Yes | No | No | Yes | No | Yes | TR14E5211 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2917 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0609 | Mitsubishi Electric | Ecodan | PUZ-WM60VAA | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PUZ-WM60VAA | Heat pump | PUZ-WM60VAA.UK 0B00001 | 13 | 2.99 | DoC_PUZ-WM60-85VAA.pdf | CE2020C08 | EN 61000-3-12 | EN 61000-3-11 | TR19E40110 H&F + PUZ-WM60VAA+PUZ-WM85VAA Flicker TR20EZ101 | TR19E40110 + TR20EZ101 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM85VAA Databook | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0610 | Mitsubishi Electric | Ecodan | PUZ-WM85VAA | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | PUZ-WM85VAA | Heat pump | PUZ-WM85VAA.UK 0A00001 | 22 | 5.06 | DoC_PUZ-WM60-85VAA.pdf | CE2020C08 | EN 61000-3-12 | EN 61000-3-11 | TR19E40110 H&F + PUZ-WM60VAA+PUZ-WM85VAA Flicker TR20EZ101 | TR19E40110 + TR20EZ101 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM85VAA Databook | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0611 | Mitsubishi Electric | Ecodan | PUZ-WM112VAA | Heating only | Air Source | 1 | 230 |  |  |  |  | 28 | 6.44 | 28 | 6.44 | PUZ-WM112VAA | Heat pump | PUZ-WM112VAA.UK 0B00006 | 28 | 6.44 | DoC_PUZ-WM112VAA | CE2020C08 | EN 61000-3-12 | EN 61000-3-11 | TR19E40112 H&F + PUZ-WM112VAA Flicker TR20EZ102 | TR19E40112 + TR20EZ102 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM112VAA Databook | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0612 | Mitsubishi Electric | Ecodan | PUZ-HWM140VHA | Heating only | Air Source | 1 | 230 |  |  |  |  | 35 | 8.05 | 35 | 8.05 | PUZ-HWM140VHA | Heat pump | PUZ-HWM140VHA 00T00000 | 35 | 8.05 | 20-110770 EU Type Examination Certificate EMCD.pdf | 20-110770 | EN 61000-3-12 | EN 61000-3-11 | TR20E2203 H&F.pdf + PUZ-HWM140VHA TR20EZ103.pdf | TR20E2203 + TR20EZ103 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0613 | Mitsubishi Electric | Ecodan | PUZ-HWM140YHA | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | PUZ-HWM140YHA | Heat pump | PUZ-HWM140YHA 00T00000 | 13 | 9 | 20-110771 EU Type Examination Certificate EMCD.pdf | 20-110771 | EN 61000-3-2 | EN 61000-3-3 | TR20E2204 H&F.pdf | TR20E2204 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0614 | Mitsubishi Electric | Ecodan | PUZ-WM85YAA | Heating only | Air Source | 3 | 400 |  |  |  |  | 11.5 | 7.97 | 11.5 | 7.97 | PUZ-WM85YAA | Heat pump |  | 11.5 | 7.97 | DoC_PUZ-WM85YAA.pdf | CE2020C10 | EN 61000-3-2 | EN 61000-3-3 | TR19E40113 PUZ-WM112YAA | TR19E40113 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM85YAA Databook | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0615 | Mitsubishi Electric | Ecodan | PUZ-WM112YAA | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | PUZ-WM112YAA | Heat pump |  | 13 | 9.01 | DoC_PUZ-WM112YAA.pdf | CE2020C10 | EN 61000-3-2 | EN 61000-3-3 | TR19E40113 PUZ-WM112YAA | TR19E40113 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM112YAA Databook | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0616 | Mitsubishi Electric | CAHV | CAHV-P500YB-HPB | Heating only | Air Source | 3 | 400 |  |  |  |  | 54.9 | 38.04 | 54.9 | 38.04 | CAHV-P500YB-HPB | Heat pump |  | 54.9 | 38.03 | DOC for CAHV | 15-111125a | EN 61000-3-12 | EN 61000-3-11 | CAHV Test Report | EUT15002 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4110 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.15
HP_0617 | Mitsubishi Electric | QAHV | QAHV-N560YA-HPB | Heating only | Air Source | 3 | 400 |  |  |  |  | 33.8 | 23.42 | 33.8 | 23.42 | QAHV-N560YA-HPB | Heat pump |  | 33.8 | 23.42 | Certificate for QAHV | 16-111214 | EN 61000-3-12 | EN 61000-3-11 | Test report for QAHV | EUT16002 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2620 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.23
HP_0618 | Mitsubishi Electric | CRHV | P600YA-HPB | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 44 | 30.48 | 44 | 30.48 | P600YA-HPB | Heat pump |  | 44 | 31.63 | Certificate for CRHV | 14-110636 | EN 61000-3-12 | EN 61000-3-11 | Test report for CRHV | EUT14001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 3420 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18
HP_0619 | Mitsubishi Electric | Mr Slim | PUZ-ZM140VKA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 29.5 | 6.785 | 29.5 | 6.785 | PUZ-ZM140VKA | Heat pump |  | 29.5 | 6.785 | DoC PUZ-ZM125140VKA | CE2017C04 | EN 61000-3-12 | EN 61000-3-11 | Test Report for PUZ-ZM140VKA | TR16E8051-B_PUZ-ZM140VKA | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 14 | 0.072 | 0.735 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0620 | Mitsubishi Electric | Mr Slim | PUZ-ZM125VKA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 26.5 | 6.095 | 26.5 | 6.095 | PUZ-ZM125VKA | Heat pump |  | 26.5 | 6.095 | DoC PUZ-ZM125140VKA | CE2017C04 | EN 61000-3-12 | EN 61000-3-11 | Test Report for PUZ-ZM140VKA | TR16E8051-B_PUZ-ZM140VKA | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 14 | 0.072 | 0.735 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0621 | Mitsubishi Electric | Mr Slim | PUZ-ZM100VKA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 26.5 | 6.095 | 26.5 | 6.095 | PUZ-ZM100VKA | Heat pump |  | 26.5 | 6.095 | 20200218_DOC_PUZ-ZM100VKA | CE2020C02 | EN 61000-3-12 | EN 61000-3-11 | Test Report for PUZ-ZM140VKA | TR16E8051-B_PUZ-ZM140VKA | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 14 | 0.072 | 0.735 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0622 | Mitsubishi Electric | PUZ-ZM | PUZ-ZM100YKA | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 10.7 | 7.41 | 10.7 | 7.41 | PUZ-ZM100YKA | Whole system |  | 10.7 | 7.41 | PUZ-ZM100YKA_DoC_(CE2020C03) | CE2020C03 | EN 61000-3-2 | EN 61000-3-3 | PUZ-ZM100-140YKA_Electrical_Tests_(TR16EY113) | TR16EY113 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-ZM100YKA_DoC_(CE2020C03) | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0623 | Mitsubishi Electric | City Multi | PUMY-P112YKM4 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | PUMY-P112YKM4 | Heat pump |  | 13 | 5.2 | DoC_PUMY-P112125140YKM4 | CE2020A05 | EN 61000-3-2 | EN 61000-3-3 | Test report PUMY-P112125140YKM | TR17E6171 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0624 | Mitsubishi Electric | City Multi | PUMY-P125YKM4 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | PUMY-P125YKM4 | Heat pump |  | 13 | 5.2 | DoC_PUMY-P112125140YKM4 | CE2020A05 | EN 61000-3-2 | EN 61000-3-3 | Test report PUMY-P112125140YKM | TR17E6171 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0625 | Mitsubishi Electric | City Multi | PUMY-P140YKM4 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | PUMY-P140YKM4 | Heat pump |  | 13 | 5.2 | DoC_PUMY-P112125140YKM4 | CE2020A05 | EN 61000-3-2 | EN 61000-3-3 | Test report PUMY-P112125140YKM | TR17E6171 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0626 | Mitsubishi Electric | City Multi | PUMY-P200YKM2 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 19 | 13.163 | 19 | 13.163 | PUMY-P200YKM2 | Heat pump |  | 19 | 13.163 | DoC_PUMY-P200YKM2 | CE2020A06 | EN 61000-3-12 | EN 61000-3-11 | Test report PUMY-P200 | S1762901 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1579 |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
HP_0627 | Mitsubishi Electric | City Multi | PUMY-P112VKM5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 29.5 | 6.785 | 29.5 | 6.785 | PUMY-P112VKM5 | Heat pump |  | 29.5 | 6.785 | DoC_PUMY-P112125140VKM5 | CE2020A04 | EN 61000-3-12 | EN 61000-3-11 | Test report PUMY-P112125140VKM | T19Z3401 | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0628 | Mitsubishi Electric | City Multi | PUMY-P125VKM5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 29.5 | 6.785 | 29.5 | 6.785 | PUMY-P125VKM5 | Heat pump |  | 29.5 | 6.785 | DoC_PUMY-P112125140VKM5 | CE2020A04 | EN 61000-3-12 | EN 61000-3-11 | Test report PUMY-P112125140VKM | T19Z3401 | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0629 | Mitsubishi Electric | City Multi | PUMY-P140VKM5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 29.5 | 6.785 | 29.5 | 6.785 | PUMY-P140VKM5 | Heat pump |  | 29.5 | 6.785 | DoC_PUMY-P112125140VKM5 | CE2020A04 | EN 61000-3-12 | EN 61000-3-11 | Test report PUMY-P112125140VKM | T19Z3401 | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0630 | Mitsubishi Electric | City Multi | PUMY-SP112VKM | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.5 | 7.015 | 30.5 | 7.015 | PUMY-SP112VKM | Heat pump |  | 30.5 | 7.015 | DoC_PUMY-SP112125140VKM | CE2020B13 | EN 61000-3-12 | EN 61000-3-11 | Test report PUMY-SP112125140VKM | T17E3221-A | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0631 | Mitsubishi Electric | City Multi | PUMY-SP125VKM | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.5 | 7.015 | 30.5 | 7.015 | PUMY-SP125VKM | Heat pump |  | 30.5 | 7.015 | DoC_PUMY-SP112125140VKM | CE2020B13 | EN 61000-3-12 | EN 61000-3-11 | Test report PUMY-SP112125140VKM | T17E3221-A | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0632 | Mitsubishi Electric | City Multi | PUMY-SP140VKM | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.5 | 7.015 | 30.5 | 7.015 | PUMY-SP140VKM | Heat pump |  | 30.5 | 7.015 | DoC_PUMY-SP112125140VKM | CE2020B13 | EN 61000-3-12 | EN 61000-3-11 | Test report PUMY-SP112125140VKM | T17E3221-A | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0633 | Mitsubishi Electric | City Multi | PURY-P200YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | PURY-P200YNW-A | Heat pump |  | 16.1 | 11.2 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1050 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0634 | Mitsubishi Electric | City Multi | PURY-P300YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 22.7 | 15.73 | 22.7 | 15.73 | PURY-P300YNW-A | Heat pump |  | 22.7 | 15.7 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1640 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0635 | Mitsubishi Electric | City Multi | PURY-P350YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | PURY-P350YNW-A | Heat pump |  | 27.6 | 19.12 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1870 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.27612
HP_0636 | Mitsubishi Electric | City Multi | PURY-P400YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 35.1 | 24.32 | 35.1 | 24.32 | PURY-P400YNW-A | Heat pump |  | 35.1 | 24.32 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2160 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.21713
HP_0637 | Mitsubishi Electric | City Multi | PURY-P450YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 37.1 | 25.7 | 37.1 | 25.7 | PURY-P450YNW-A | Heat pump |  | 37.1 | 25.7 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2310 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.20542
HP_0638 | Mitsubishi Electric | City Multi | PURY-P500YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 43.2 | 29.93 | 43.2 | 29.93 | PURY-P500YNW-A | Heat pump |  | 43.2 | 29.93 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 3090 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.17641
HP_0639 | Mitsubishi Electric | City Multi | PURY-EP450YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 34.6 | 23.97 | 34.6 | 23.97 | PURY-EP450YNW-A | Heat pump |  | 34.6 | 24 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2140 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.22026
HP_0640 | Mitsubishi Electric | City Multi | PURY-EP500YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 40.3 | 27.92 | 40.3 | 27.92 | PURY-EP500YNW-A | Heat pump |  | 40.3 | 27.9 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2830 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18911
HP_0641 | Mitsubishi Electric | City Multi | PURY-EP200YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | PURY-EP200YNW-A | Heat pump |  | 16.1 | 11.2 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1070 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0642 | Mitsubishi Electric | City Multi | PURY-EP250YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 17 | 11.78 | 17 | 11.78 | PURY-EP250YNW-A | Heat pump |  | 17 | 11.8 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1210 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0643 | Mitsubishi Electric | City Multi | PURY-EP300YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 20.3 | 14.06 | 20.3 | 14.06 | PURY-EP300YNW-A | Heat pump |  | 20.3 | 14.1 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1460 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0644 | Mitsubishi Electric | City Multi | PURY-EP350YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.4 | 16.9 | 24.4 | 16.9 | PURY-EP350YNW-A | Heat pump |  | 24.4 | 16.9 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1720 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0645 | Mitsubishi Electric | City Multi | PURY-EP400YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 30.7 | 21.27 | 30.7 | 21.27 | PURY-EP400YNW-A | Heat pump |  | 30.7 | 21.3 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1970 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.248
HP_0646 | Mitsubishi Electric | City Multi | PURY-EP550YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 44.3 | 30.69 | 44.3 | 30.69 | PURY-EP550YNW-A | Heat pump |  | 44.3 | 30.7 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2900 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.172
HP_0647 | Mitsubishi Electric | City Multi | PURY-P250YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 17.8 | 12.33 | 17.8 | 12.33 | PURY-P250YNW-A | Heat pump |  | 17.8 | 12.3 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1240 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0648 | Mitsubishi Electric | City Multi | PURY-P550YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 47.5 | 32.91 | 47.5 | 32.91 | PURY-P550YNW-A | Heat pump |  | 47.5 | 32.9 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 3490 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.16
HP_0649 | Mitsubishi Electric | Mr Slim | PUZ-ZM35VKA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PUZ-ZM35VKA | Heat pump |  | 13 | 2.99 | DoC_PUZ-ZM3550VKA | CE2020A13 | EN 61000-3-2 | EN 61000-3-3 | Test Report for PUZ-ZM50VKA | TR16E7182_PUZ-ZM50VKA | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0650 | Mitsubishi Electric | Mr Slim | PUZ-ZM50VKA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PUZ-ZM50VKA | Heat pump |  | 13 | 2.99 | DoC_PUZ-ZM3550VKA | CE2020A13 | EN 61000-3-2 | EN 61000-3-3 | Test Report for PUZ-ZM50VKA | TR16E7182_PUZ-ZM50VKA | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0651 | Mitsubishi Electric | City Multi | PUHY-P200YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | PUHY-P200YNW-A | Heat pump |  | 16.1 | 11.1 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1060 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0652 | Mitsubishi Electric | City Multi | PUHY-P250YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 17.8 | 12.33 | 17.8 | 12.33 | PUHY-P250YNW-A | Heat pump |  | 17.8 | 12.3 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1240 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0653 | Mitsubishi Electric | City Multi | PUHY-P300YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 22.7 | 15.73 | 22.7 | 15.73 | PUHY-P300YNW-A | Heat pump |  | 22.7 | 15.7 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1640 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0654 | Mitsubishi Electric | City Multi | PUHY-P350YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 26.4 | 18.29 | 26.4 | 18.29 | PUHY-P350YNW-A | Heat pump |  | 26.4 | 18.3 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1810 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2886
HP_0655 | Mitsubishi Electric | City Multi | PUHY-P400YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 31.9 | 22.1 | 31.9 | 22.1 | PUHY-P400YNW-A | Heat pump |  | 31.9 | 22.1 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2010 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2389
HP_0656 | Mitsubishi Electric | City Multi | PUHY-P450YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 37.1 | 25.7 | 37.1 | 25.7 | PUHY-P450YNW-A | Heat pump |  | 37.1 | 25.7 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2310 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2054
HP_0657 | Mitsubishi Electric | City Multi | PUHY-P500YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 43.7 | 30.28 | 43.7 | 30.28 | PUHY-P500YNW-A | Heat pump |  | 43.7 | 30.28 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 3080 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.1744
HP_0658 | Mitsubishi Electric | City Multi | PUHY-M200YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.1544 | 16.1 | 11.1544 | PUHY-M200YNW-A1 | Heat pump |  | 16.1 | 11.1544 | Test Certificate PURY-PUHY |  | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1030 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0659 | Mitsubishi Electric | City Multi | PUHY-M250YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 17.8 | 12.3322 | 17.8 | 12.3322 | PUHY-M250YNW-A1 | Heat pump |  | 17.8 | 12.3322 | Test Certificate PURY-PUHY |  | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1130 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0660 | Mitsubishi Electric | City Multi | PUHY-EP200YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | PUHY-EP200YNW-A | Heat pump |  | 16.1 | 11.1 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1090 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0661 | Mitsubishi Electric | City Multi | PUHY-EP250YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.4 | 11.36 | 16.4 | 11.36 | PUHY-EP250YNW-A | Heat pump |  | 16.4 | 11.4 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1170 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0662 | Mitsubishi Electric | City Multi | PUHY-EP300YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 20.3 | 14.06 | 20.3 | 14.06 | PUHY-EP300YNW-A | Heat pump |  | 20.3 | 14.06 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1470 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0663 | Mitsubishi Electric | City Multi | PUHY-EP350YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.1 | 16.7 | 24.1 | 16.7 | PUHY-EP350YNW-A | Heat pump |  | 24.1 | 16.7 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1720 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0664 | Mitsubishi Electric | City Multi | PUHY-EP400YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 28.2 | 19.54 | 28.2 | 19.54 | PUHY-EP400YNW-A | Heat pump |  | 28.2 | 19.5 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1860 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
HP_0665 | Mitsubishi Electric | City Multi | PUHY-EP450YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 33.7 | 23.35 | 33.7 | 23.35 | PUHY-EP450YNW-A | Heat pump |  | 33.7 | 23.3 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2070 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.21
HP_0666 | Mitsubishi Electric | City Multi | PUHY-EP500YNW-A | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 40.8 | 28.27 | 40.8 | 28.27 | PUHY-EP500YNW-A | Heat pump |  | 40.8 | 28.3 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | EUT16006A_170414.pdf | EUT16006A | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2910 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18
HP_0667 | Mitsubishi Electric | City Multi | PUHY-M300YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 22.7 | 15.727 | 22.7 | 15.727 | PUHY-M300YNW-A1 | Heat pump |  | 22.7 | 15.727 | Test Certificate PURY-PUHY R410-A | EU-TYPE EXAMINATION CERTIFICATE No. 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1420 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0668 | Mitsubishi Electric | City Multi | PURY-M200YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.1544 | 16.1 | 11.1544 | PURY-M200YNW-A1 | Heat pump |  | 16.1 | 11.1544 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1040 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0669 | Mitsubishi Electric | City Multi | PURY-M250YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 20.4 | 14.1335 | 20.4 | 14.1335 | PURY-M250YNW-A1 | Heat pump |  | 20.4 | 14.1335 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1310 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0670 | Mitsubishi Electric | City Multi | PURY-M300YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 25.1 | 17.3898 | 25.1 | 17.3898 | PURY-M300YNW-A1 | Heat pump |  | 25.1 | 17.3898 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1570 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0671 | Mitsubishi Electric | City Multi | PURY-M350YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.1218 | 27.6 | 19.1218 | PURY-M350YNW-A1 | Heat pump |  | 27.6 | 19.1218 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1760 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.27612
HP_0672 | Mitsubishi Electric | City Multi | PURY-M400YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 35.1 | 24.318 | 35.1 | 24.318 | PURY-M400YNW-A1 | Heat pump |  | 35.1 | 24.318 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2300 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.21712
HP_0673 | Mitsubishi Electric | City Multi | PURY-M450YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 37.1 | 25.7036 | 37.1 | 25.7036 | PURY-M450YNW-A1 | Heat pump |  | 37.1 | 25.7036 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2460 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.20542
HP_0674 | Mitsubishi Electric | City Multi | PURY-M500YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 43.2 | 29.9298 | 43.2 | 29.9298 | PURY-M500YNW-A1 | Heat pump |  | 43.2 | 29.9298 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2990 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.17641
HP_0675 | Mitsubishi Electric | City Multi | PURY-EM200YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.1544 | 16.1 | 11.1544 | PURY-EM200YNW-A1 | Heat pump |  | 16.1 | 11.1544 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1030 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0676 | Mitsubishi Electric | City Multi | PURY-EM250YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 19.8 | 13.7178 | 19.8 | 13.7178 | PURY-EM250YNW-A1 | Heat pump |  | 19.8 | 13.7178 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1260 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0677 | Mitsubishi Electric | City Multi | PURY-EM300YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.4 | 16.212 | 23.4 | 16.212 | PURY-EM300YNW-A1 | Heat pump |  | 23.4 | 16.212 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1440 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0678 | Mitsubishi Electric | City Multi | PURY-EM350YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.4 | 16.9048 | 24.4 | 16.9048 | PURY-EM350YNW-A1 | Heat pump |  | 24.4 | 16.9048 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1540 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0679 | Mitsubishi Electric | City Multi | PURY-EM400YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 30.7 | 21.2696 | 30.7 | 21.2696 | PURY-EM400YNW-A1 | Heat pump |  | 30.7 | 21.2696 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2000 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2482
HP_0680 | Mitsubishi Electric | City Multi | PURY-EM450YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 34.6 | 23.9716 | 34.6 | 23.9716 | PURY-EM450YNW-A1 | Heat pump |  | 34.6 | 23.9716 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2280 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2203
HP_0681 | Mitsubishi Electric | City Multi | PURY-EM500YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 40.3 | 27.9207 | 40.3 | 27.9207 | PURY-EM500YNW-A1 | Heat pump |  | 40.3 | 27.9207 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2740 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18911
HP_0682 | Mitsubishi Electric | City Multi | PUHY-EM200YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.1544 | 16.1 | 11.1544 | PUHY-EM200YNW-A1 | Heat pump |  | 16.1 | 11.1544 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1020 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0683 | Mitsubishi Electric | City Multi | PUHY-EM250YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 16.4 | 11.3623 | 16.4 | 11.3623 | PUHY-EM250YNW-A1 | Heat pump |  | 16.4 | 11.3623 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1030 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0684 | Mitsubishi Electric | City Multi | PUHY-EM300YNW-A1 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 20.3 | 14.0643 | 20.3 | 14.0643 | PUHY-EM300YNW-A1 | Heat pump |  | 20.3 | 14.0643 | Test Certificate PURY-PUHY | 20-111658 | EN 61000-3-12 | EN 61000-3-11 | Test Data PURY-PUHY R32 EUT18003 | EUT18003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1240 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0685 | Mitsubishi Electric | Ecodan | PUHZ-ZRP200YKA | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 19 | 13.16 | 19 | 13.16 | PUHZ-ZRP200YKA | Heat pump |  | 19 | 13.16 | PUHZ-ZRP200250_Declaration_of_Conformity__CE2014C18_ | CE2014C18 | EN 61000-3-12 | EN 61000-3-11 | TR14E5211 | TR14E5211_PUHZ-ZRP200250YKA | No | Yes | No | No | Yes | No | Yes | TR14E5211 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2917 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0686 | Mitsubishi Electric | Ecodan | PUZ-WM50VHA | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PUZ-WM50VHA | Heat pump | PUZ-WM50VHA.UK 0A00001 | 13 | 2.99 | DoC_PUZ-WM50VHA.pdf | CE2020C11 | EN 61000-3-2 | EN 61000-3-3 | TR19E6211.pdf | TR19E6211 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM50VHA Databook | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0687 | Mitsubishi Electric | Ecodan | PUZ-WM60VAA | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PUZ-WM60VAA | Heat pump | PUZ-WM60VAA.UK 0B00001 | 13 | 2.99 | DoC_PUZ-WM60-85VAA.pdf | CE2020C08 | EN 61000-3-12 | EN 61000-3-11 | TR19E40110 H&F + PUZ-WM60VAA+PUZ-WM85VAA Flicker TR20EZ101 | TR19E40110 + TR20EZ101 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM85VAA Databook | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0688 | Mitsubishi Electric | Ecodan | PUZ-WM85VAA | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | PUZ-WM85VAA | Heat pump | PUZ-WM85VAA.UK 0A00001 | 22 | 5.06 | DoC_PUZ-WM60-85VAA.pdf | CE2020C08 | EN 61000-3-12 | EN 61000-3-11 | TR19E40110 H&F + PUZ-WM60VAA+PUZ-WM85VAA Flicker TR20EZ101 | TR19E40110 + TR20EZ101 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM85VAA Databook | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0689 | Mitsubishi Electric | Ecodan | PUZ-WM112VAA | Heating only | Air Source | 1 | 230 |  |  |  |  | 28 | 6.44 | 28 | 6.44 | PUZ-WM112VAA | Heat pump | PUZ-WM112VAA.UK 0B00006 | 28 | 6.44 | DoC_PUZ-WM112VAA | CE2020C08 | EN 61000-3-12 | EN 61000-3-11 | TR19E40112 H&F + PUZ-WM112VAA Flicker TR20EZ102 | TR19E40112 + TR20EZ102 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM112VAA Databook | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  | TR19E40112 + TR20EZ102 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0690 | Mitsubishi Electric | Ecodan | PUZ-HWM140VHA | Heating only | Air Source | 1 | 230 |  |  |  |  | 35 | 8.05 | 35 | 8.05 | PUZ-HWM140VHA | Heat pump | PUZ-HWM140VHA 00T00000 | 35 | 8.05 | 20-110770 EU Type Examination Certificate EMCD.pdf | 20-110770 | EN 61000-3-12 | EN 61000-3-11 | TR20E2203 H&F.pdf + PUZ-HWM140VHA TR20EZ103.pdf | TR20E2203 + TR20EZ103 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0691 | Mitsubishi Electric | Ecodan | PUZ-HWM140YHA | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | PUZ-HWM140YHA | Heat pump | PUZ-HWM140YHA 00T00000 | 13 | 9 | 20-110771 EU Type Examination Certificate EMCD.pdf | 20-110771 | EN 61000-3-2 | EN 61000-3-3 | TR20E2204 H&F.pdf | TR20E2204 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0692 | Mitsubishi Electric | Ecodan | PUZ-WM85YAA | Heating only | Air Source | 3 | 400 |  |  |  |  | 11.5 | 7.97 | 11.5 | 7.97 | PUZ-WM85YAA | Heat pump |  | 11.5 | 7.97 | DoC_PUZ-WM85YAA.pdf | CE2020C10 | EN 61000-3-2 | EN 61000-3-3 | TR19E40113 PUZ-WM112YAA | TR19E40113 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM85YAA Databook | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0693 | Mitsubishi Electric | Ecodan | PUZ-WM112YAA | Heating only | Air Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | PUZ-WM112YAA | Heat pump |  | 13 | 9.01 | DoC_PUZ-WM112YAA.pdf | CE2020C10 | EN 61000-3-2 | EN 61000-3-3 | TR19E40113 PUZ-WM112YAA | TR19E40113 | Yes | Yes | Yes | Yes | Yes | Yes | No | PUZ-WM112YAA Databook | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Water (immersion) heater - external (see Note 1 below) |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0401 | Nibe | F1155 | F1155-6 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 33 | 7.59 | 33 | 7.59 | F1155-6 | Whole system |  | 33 | 7.59 | 1155 DOC.PDF | DOC_0000543-1 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes | No | No | Yes | Form J1 - F1155F1255-6 R 1x230 UK.PDF | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0402 | Nibe | F1255 | F1255-6 R 1x230 UK | Heating only | Ground Source | 1 | 230 |  |  |  |  | 33 | 7.59 | 33 | 7.59 | F1255-6 R 1x230 UK | Whole system |  | 33 | 7.59 | 1155 DOC.PDF | DOC_0000543-1 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes | No | No | Yes | Form J1 - F1155F1255-6 R 1x230 UK.PDF | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0403 | Nibe | F1255 | F1255-12 R 1x230 UK | Heating only | Ground Source | 1 | 230 |  |  |  |  | 52 | 11.96 | 52 | 11.96 | F1255-12 R 1x230 UK | Whole system |  | 52 | 11.96 | 1255 DOC.PDF | DOC_0001273-1 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes | No | No | Yes | Form J1 - F1155F1255-12 R 1x230 UK.PDF | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0404 | Nibe | F2040 | F2040-6 | Heating & Cooling | Air Source | 1 | 230 | 7.78 |  |  |  | 15 | 3.45 | 15 | 3.45 | F2040-6 | Whole system |  | 15 | 3.45 | F2040-6 DOC.PDF | DOC_0001474-0 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Form J1 - F2040-6.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0405 | Nibe | F2040 | F2040-8 | Heating & Cooling | Air Source | 1 | 230 | 10.7 |  |  |  | 15.65 | 3.6 | 15.65 | 3.6 | F2040-8 | Whole system |  | 15.65 | 3.6 | F2040-8 and 12 DOC.PDF | DOC_0000461-1 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | DOC_0001318-0 NIBE F2040-8 UK Form J1.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0406 | Nibe | F2040 | F2040-12 | Heating & Cooling | Air Source | 1 | 230 | 14.22 |  |  |  | 23.04 | 5.3 | 23.04 | 5.3 | F2040-12 | Whole system |  | 23.04 | 5.3 | F2040-8 and 12 DOC.PDF | DOC_0000461-1 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | DOC_0001319-3 NIBE F2040-16 UK Form J2.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0407 | Nibe | F2040 | F2040-16 | Heating & Cooling | Air Source | 1 | 230 | 18.78 |  |  |  | 25 | 5.75 | 25 | 5.75 | F2040-16 | Whole system |  | 25 | 5.75 | F2040-16 DOC.PDF | DOC_0000462-1 | EN 61000-3-12 | EN 61000-3-11 |  |  | No | No | No | No | Yes | No | Yes | DOC_0001319-3 NIBE F2040-16 UK Form J2.pdf | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.109 | 0.484 | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0408 | Nibe | F1345 | F1345-24 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 20.5 | 14.2 | 20.5 | 14.2 | F1345-24 | Whole system |  | 20.5 | 8.2 | F1345 - DOC.pdf | DOC 0887 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report 1408674STO-001, Ed 1.pdf | 1408674STO-001 | No | Yes | No | No | Yes | No | Yes | Form J1 F1345-24 3x400 UK (6).doc | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_0409 | Nibe | F1345 | F1345-30 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 25.3 | 17.53 | 25.3 | 17.53 | F1345-30 | Whole system |  | 25.3 | 10.1 | F1345 - DOC.pdf | DOC 0887 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report 1408674STO-002, Ed 1.pdf | 1408674STO-002 | No | Yes | No | No | Yes | No | Yes | Form J1 F1345-30 3x400 UK.doc | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_0410 | Nibe | F1345 | F1345-40 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 29.5 | 20.44 | 29.5 | 20.44 | F1345-40 | Whole system |  | 29.5 | 11.8 | F1345 - DOC.pdf | DOC 0887 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report 1408674STO-003, Ed 1.pdf | 1408674STO-003 | No | Yes | No | No | Yes | No | Yes | Form J1 F1345-40 3x400 UK.doc | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_0411 | Nibe | F1345 | F1345-60 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 44.3 | 30.69 | 44.3 | 30.69 | F1345-60 | Whole system |  | 44.3 | 17.7 | F1345 - DOC.pdf | DOC 0887 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report 1408674STO-004 Ed 1.pdf | 1408674STO-004 | No | No | No | No | No | No | Yes | Form J1 F1345-60 3x400 UK.doc | Equipment complying with IEC 61000-3-12 |  |  | 9 | 0.276 | 0.579 | Requires Zsource ≤Zmax | 0.39 | Yes | No |  | Yes | No |  | Yes | No
HP_0412 | Nibe | F1145 | F1145-15 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | Nibe F1145-15 | Whole system |  | 26 | 10.4 | DOC_00011468-0.pdf | 00011468-0 | EN 61000-3-12 | EN 61000-3-11 | Test report F1145-15.pdf | 14155-02H | No | Yes | No | No | Yes | No | Yes | Form J2 F1145-15 EXP.doc | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  |  | No |  | Yes | No
HP_0413 | Nibe | F1145 | F1145-17 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 28 | 19.4 | 28 | 19.4 | Nibe F1145-17 | Whole system |  | 28 | 11.2 | DOC_0001388-0.pdf | 0001388-0 | EN 61000-3-12 | EN 61000-3-11 | Test report F1145-17.pdf | 14156-01H | No | Yes | No | No | Yes | No | Yes | Form J2 F1145-17 EXP (5).doc | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.5404 | 0.296 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_0414 | Nibe | F1155 | F1155-12 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 52.2 | 12.01 | 52.2 | 12.01 | Nibe F1155-12 | Whole system |  | 52.2 | 12.01 | DOC_0001273 | DOC_0001273 | EN 61000-3-12 | EN 61000-3-11 | EMC TEST REPORT F1155-12 230V 1515621STO-001, ED1 | 1515621STO-001 | Yes | Yes | Yes | Yes | No | No | Yes | Form J1 - F1155F1255-12 R 1x230 UK | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_0415 | Nibe | S1155 | S1155-6 EM 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 32.8 | 7.54 | 32.8 | 7.54 | S1155-6 EM 1x230V | Heat pump |  | 13.23 | 3 | S1155-6 EM 1X230V DOC | DOC_0002140-0 | EN 61000-3-12 | EN 61000-3-11 | 1817000STO-001, Ed 1 | 1817000STO-001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
[16 empty] | 4.5kW Immersion | Back-up heater - on-board |  | 19.57 | 4.5 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
HP_0416 | Nibe | S1155 | S1155-12 EM 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 52.2 | 12.01 | 52.2 | 12.01 | S1155-12 EM 1x230V | Heat pump |  | 21.8 | 4.94 | S1155-12 EM 1X230V DOC | DOC_0002138-0 | EN 61000-3-12 | EN 61000-3-11 | 1816999STO-001, Ed 1 | 1816999STO-001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 21 | 0.099 | 0.532 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
[16 empty] | 7kW immersion | Back-up heater - on-board |  | 30.4 | 7 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
HP_0417 | Nibe | S1255 | S1255-6 EM 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 32.8 | 7.54 | 32.8 | 7.54 | S1255-6 EM 1x230V | Heat pump |  | 13.23 | 3 | S1255-6 R EN 1X230V UK DOC | DOC_0002141-0 | EN 61000-3-12 | EN 61000-3-11 | 1817000STO-001, Ed 1 | 1817000STO-001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
[16 empty] | 4.5kW Immersion | Back-up heater - on-board |  | 19.57 | 4.5 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
HP_0418 | Nibe | S1255 | S1255-12 EM 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 52.2 | 12.01 | 52.2 | 12.01 | S1255-12 EM 1x230V | Heat pump |  | 21.8 | 4.94 | S1255-12 R EM 1X230V UK DOC | DOC_0002139-0 | EN 61000-3-12 | EN 61000-3-11 | 1816999STO-001, Ed 1 | 1816999STO-001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.09221 | 0.57371 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
[16 empty] | 7kW immersion | Back-up heater - on-board |  | 30.4 | 7 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
HP_0419 | Nibe | F1355 | F1355-43 3x400V | Heating only | Ground Source | 3 | 400 |  |  |  |  | 30.5 | 21.13 | 30.5 | 21.13 | F1355-43 3x400V | Whole system |  | 30.5 | 21.13 | DOC_0001374-2 | DOC_0001374-2 | EN 61000-3-12 | EN 61000-3-11 | EMC HELIX45 1816042STO-001 ed 1 | 1816042STO-001 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 22 | 0.15433 | 0.343 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | Yes | Yes | Stepped
HP_0420 | Nibe | S1155 | S1155-16 EM 3x400V | Heating only | Ground Source | 3 | 400 |  |  |  |  | 24 | 16.63 | 24 | 16.63 | S1155-16 EM 3x400V | Heat pump |  | 10 | 6.9 | S1155-16 EM 3X400V DOC | DOC_0001909-0 | EN 61000-3-12 | EN 61000-3-11 | 1817001STO-001, Ed 1 | 1817001STO-001, Ed 1 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2000 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
[16 empty] | 9kW immersion | Back-up heater - on-board |  | 14 | 9.7 | [9 empty] | No | No | No | Yes |  |  |  |  | N/A | N/A | N/A |  |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
HP_0421 | Nibe | F1355-28 | F1355-28 3x400 UK | Heating & Cooling | Ground Source | 3 | 400 |  |  |  |  | 22.1 | 15.31 | 22.1 | 15.31 | F1355-28 3x400 UK | Whole system |  | 22.1 | 15.3 | DOC_0001374-0 | DOC_0001374 | EN 61000-3-12 | EN 61000-3-11 | REC-E704777 rev. A | REC-E704777 rev. A | No | Yes | No | No | Yes | No | Yes | REC-E704777 rev. A | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes |  | Yes | Yes |  | Yes | No
HP_0422 | Nibe | S1155 | S1155-25 EM 3x400V | Heating only | Ground Source | 3 | 400 |  |  |  |  | 29 | 20.09 | 29 | 20.09 | S1155-25 EM 3x400V | Heat pump |  | 14 | 9.9 | DOC_0002254-0 | 0002254-0 | EN 61000-3-12 | EN 61000-3-11 | 1907806STO-001, Ed 1 | 1907806 | No | Yes | No | No | Yes | No | Yes | S1155 Installer Manual | Equipment complying with IEC 61000-3-12 |  |  | 25 | 0.5023 | 0.319 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | Stepped | Yes | Yes | Stepped | No | No | NA
[16 empty] | 9kW Immersion | Back-up heater - on-board |  | 14.3 | 9 |  |  | EN 61000-3-12 | EN 61000-3-11 | [5 empty] | No |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_0423 | Nibe | F2040 | F2040-6 | Heating & Cooling | Air Source | 1 | 230 | 7.78 |  |  |  | 15 | 3.45 | 15 | 3.45 | F2040-6 | Whole system |  | 15 | 3.45 | F2040-6 DOC.PDF | DOC_0001474-0 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Form J1 - F2040-6.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Water (immersion) heater - external |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0424 | Nibe | F2040 | F2040-8 | Heating & Cooling | Air Source | 1 | 230 | 10.7 |  |  |  | 15.65 | 3.6 | 15.65 | 3.6 | F2040-8 | Whole system |  | 15.65 | 3.6 | F2040-8 and 12 DOC.PDF | DOC_0000461-1 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | DOC_0001318-0 NIBE F2040-8 UK Form J1.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Water (immersion) heater - external |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0425 | Nibe | F2040 | F2040-12 | Heating & Cooling | Air Source | 1 | 230 | 14.22 |  |  |  | 23.04 | 5.3 | 23.04 | 5.3 | F2040-12 | Whole system |  | 23.04 | 5.3 | F2040-8 and 12 DOC.PDF | DOC_0000461-1 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | DOC_0001319-3 NIBE F2040-16 UK Form J2.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - external |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0426 | Nibe | F2040 | F2040-16 | Heating & Cooling | Air Source | 1 | 230 | 18.78 |  |  |  | 25 | 5.75 | 25 | 5.75 | F2040-16 | Whole system |  | 25 | 5.75 | F2040-16 DOC.PDF | DOC_0000462-1 | EN 61000-3-12 | EN 61000-3-11 |  |  | No | No | No | No | Yes | No | Yes | DOC_0001319-3 NIBE F2040-16 UK Form J2.pdf | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.109 | 0.484 | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Water (immersion) heater - external |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0427 | Nibe | S2125 | S2125-8kW 1x230 | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 3 | 13 | 3 | S2125-8 | Heat pump |  | 13 | 3 | DOC_0002086-1.pdf | DOC_0002086-1 | EN 61000-3-2 | EN 61000-3-3 | 483471rev01 TRF EMC.pdf | E21134.01 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not Applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0428 | Nibe | S2125 | S2125-12KW 1x230 | Heating only | Air Source | 1 | 230 |  |  |  |  | 19.6 | 4.51 | 19.6 | 4.51 | S2125-12 1x230V | Heat pump |  | 19.6 | 4.51 | DOC_0002831-1.pdf | DOC_0002831-1 | EN 61000-3-12 | EN 61000-3-3 | 483471rev01 TRF EMC.pdf | E21134.01 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0429 | Nibe | F2050 | F2050-6 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15 | 3.45 | 15 | 3.45 | F2050-6 | Heat pump |  | 15 | 3.45 | F2050-6 DOC_0003246-0 | DOC_0003246-0 | EN 61000-3-2 | EN 61000-3-3 | 445940 TRF EMC | E22091.00 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No | No | NA | No | No | NA | No | No | NA
HP_0430 | Nibe | F2050 | F2050-10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | F2050-10 | Heat pump |  | 16 | 3.68 | F2050-10 - DOC_0003245-0 | DOC_0003245-0 | EN 61000-3-2 | EN 61000-3-3 | 437668 TRF EMC | E21212.00 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No | No | NA | No | No | NA | No | No | NA
HP_0701 | Panasonic | WH-MXC12G6E5 | WH-MXC12G6E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 19.18 |  | 53.35 | 12.27 | 53.35 | 12.27 | WH-MXC12G6E5 | Heat pump |  | 29 | 6.27 | 023508,WH-MXC12G6E5,WH-MXC09G3E5,MRD-D14008-01,DoC.PDF | MRD-D14008-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12G6E5,WH-MXC09G3E5,TUEV,18005177_001,EMC-report.pdf | 18005177 001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1700 | 567 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater |  | 26.09 | 6 | 023508,WH-MXC12G6E5,WH-MXC09G3E5,MRD-D14008-01,DoC.PDF | MRD-D14008-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12G6E5,WH-MXC09G3E5,TUEV,18005177_001,EMC-report.pdf | 18005177 001 | Yes | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.207
HP_0702 | Panasonic | WH-MXC12G6E5 | WH-MXC12G6E5 | Heating only | Air Source | 1 | 230 |  |  | 19.18 |  | 53.35 | 12.27 | 53.35 | 12.27 | WH-MXC12G6E5 | Heat pump |  | 29 | 6.27 | 023508,WH-MXC12G6E5,WH-MXC09G3E5,MRD-D14008-01,DoC.PDF | MRD-D14008-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12G6E5,WH-MXC09G3E5,TUEV,18005177_001,EMC-report.pdf | 18005177 001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1250 | 417 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater |  | 26.09 | 6 | 023508,WH-MXC12G6E5,WH-MXC09G3E5,MRD-D14008-01,DoC.PDF | MRD-D14008-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12G6E5,WH-MXC09G3E5,TUEV,18005177_001,EMC-report.pdf | 18005177 001 | Yes | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.207
HP_0703 | Panasonic | WH-MXC12H6E5 | WH-MXC12H6E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 27.17 |  | 55 | 12.65 | 55 | 12.65 | WH-MXC12H6E5 | Heat pump |  | 29 | 6.27 | WH-MXC12H6E5_EMC_DoC | MRD-D17024-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1900 | 633 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-MXC12H6E5_EMC_DoC | MRD-D17024-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | Yes | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0704 | Panasonic | WH-MXC12H6E5 | WH-MXC12H6E5 | Heating only | Air Source | 1 | 230 |  |  | 27.17 |  | 55 | 12.65 | 55 | 12.65 | WH-MXC12H6E5 | Heat pump |  | 29 | 6.27 | WH-MXC12H6E5_EMC_DoC | MRD-D17024-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1450 | 483 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-MXC12H6E5_EMC_DoC | MRD-D17024-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0705 | Panasonic | WH-UX09HE5 WH-SXC09H3E5 | WH-UX09HE5 WH-SXC09H3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 19.37 |  | 42 | 9.66 | 42 | 9.66 | WH-UX09HE5 WH-SXC09H3E5 | Heat pump |  | 29 | 6.27 | WH-SXC09H3E5_WH-UX09HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC09H3E5_18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1700 | 567 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SXC09H3E5_WH-UX09HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC09H3E5_18008879_001,EMC-report | 18008879 001 | Yes | Yes | Yes | Yes |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0706 | Panasonic | WH-UX09HE5 WH-SXC09H3E5 | WH-UX09HE5 WH-SXC09H3E5 | Heating only | Air Source | 1 | 230 |  |  | 19.37 |  | 42 | 9.66 | 42 | 9.66 | WH-UX09HE5 WH-SXC09H3E5 | Heat pump |  | 29 | 6.27 | WH-SXC09H3E5_WH-UX09HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC09H3E5_18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1650 | 550 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SXC09H3E5_WH-UX09HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC09H3E5_18008879_001,EMC-report | 18008879 001 | Yes | Yes | Yes | Yes |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0707 | Panasonic | WH-MXC09H3E5 | WH-MXC09H3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 19.37 |  | 42 | 9.66 | 42 | 9.66 | WH-MXC09H3E5 | Heat pump |  | 29 | 6.27 | WH-MXC09H3E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC09H3E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1900 | 633 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MXC09H3E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-2 | EN 61000-3-3 | WH-MXC09H3E5_TUEV18007188_001EMC-report | 18007188 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0708 | Panasonic | WH-MXC09H3E5 | WH-MXC09H3E5 | Heating only | Air Source | 1 | 230 |  |  | 19.37 |  | 42 | 9.66 | 42 | 9.66 | WH-MXC09H3E5 | Heat pump |  | 29 | 6.27 | WH-MXC09H3E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC09H3E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1450 | 483 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MXC09H3E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-2 | EN 61000-3-11 | WH-MXC09H3E5_TUEV18007188_001EMC-report | 18007188 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0709 | Panasonic | WH-MDC05H3E5 | WH-MDC05H3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 9.89 |  | 26 | 5.98 | 26 | 5.98 | WH-MDC05H3E5 | Heat pump |  | 13 | 2.84 | WH-MDC05H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-3 | WH-MDC05H3E5,TUEV,18006926_001,EMC-report | 18006926 001 | Yes | Yes | Yes | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC05H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC05H3E5,TUEV,18006926_001,EMC-report | 18006926 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0710 | Panasonic | WH-MDC05H3E5 | WH-MDC05H3E5 | Heating only | Air Source | 1 | 230 |  |  | 9.89 |  | 26 | 5.98 | 26 | 5.98 | WH-MDC05H3E5 | Heat pump |  | 13 | 2.84 | WH-MDC05H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-3 | WH-MDC05H3E5,TUEV,18006926_001,EMC-report | 18006926 001 | Yes | Yes | Yes | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC05H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC05H3E5,TUEV,18006926_001,EMC-report | 18006926 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0711 | Panasonic | WH-MDC07H3E5 | WH-MDC07H3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 11.94 |  | 34 | 7.82 | 34 | 7.82 | WH-MDC07H3E5 | Heat pump |  | 21 | 4.59 | WH-MDC07H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC07H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 750 | 250 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC07H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC07H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0712 | Panasonic | WH-MDC07H3E5 | WH-MDC07H3E5 | Heating only | Air Source | 1 | 230 |  |  | 11.94 |  | 34 | 7.82 | 34 | 7.82 | WH-MDC07H3E5 | Heat pump |  | 21 | 4.59 | WH-MDC07H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC07H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 21 | 0.10143 | 0.522 | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC07H3E5_MRD-D17022-01,DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC07H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0713 | Panasonic | WH-MDC09H3E5 | WH-MDC09H3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 14.17 |  | 35.9 | 8.26 | 35.9 | 8.26 | WH-MDC09H3E5 | Heat pump |  | 22.9 | 5.01 | WH-MDC09H3E5_EMC_DoC | MRD-D17022-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC09H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 750 | 250 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC09H3E5_EMC_DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC09H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0714 | Panasonic | WH-MDC09H3E5 | WH-MDC09H3E5 | Heating only | Air Source | 1 | 230 |  |  | 14.17 |  | 35.9 | 8.26 | 35.9 | 8.26 | WH-MDC09H3E5 | Heat pump |  | 22.9 | 5.01 | WH-MDC09H3E5_EMC_DoC | MRD-D17022-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC09H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 21 | 0.1106 | 0.47827 | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC09H3E5_EMC_DoC | MRD-D17022-01 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC09H3E5_TUEV,18006927_001,EMC-report | 18006927 001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0715 | Panasonic | WH-MDC12H6E5 | WH-MDC12H6E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 18.28 |  | 50 | 11.5 | 50 | 11.5 | WH-MDC12H6E5 | Heat pump |  | 24 | 5.3 | WH-MDC12H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1100 | 367 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-MDC12H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0716 | Panasonic | WH-MDC12H6E5 | WH-MDC12H6E5 | Heating only | Air Source | 1 | 230 |  |  | 18.28 |  | 50 | 11.5 | 50 | 11.5 | WH-MDC12H6E5 | Heat pump |  | 24 | 5.3 | WH-MDC12H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-MDC12H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC12H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0717 | Panasonic | WH-MDC16H6E5 | WH-MDC16H6E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 21.27 |  | 52 | 11.96 | 52 | 11.96 | WH-MDC16H6E5 | Heat pump |  | 26 | 5.74 | WH-MDC16H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXDC16H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1100 | 367 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-MDC16H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXDC16H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0718 | Panasonic | WH-MDC16H6E5 | WH-MDC16H6E5 | Heating only | Air Source | 1 | 230 |  |  | 21.27 |  | 52 | 11.96 | 52 | 11.96 | WH-MDC16H6E5 | Heat pump |  | 26 | 5.74 | WH-MDC16H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXDC16H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-MDC16H6E5_EMC_DoC | MRD-D17024-01 | EN 61000-3-12 | EN 61000-3-11 | WH-MXDC16H6E5_TUEV18007188_001EMC-report | 18007188 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0719 | Panasonic | WH-SXC12H6E5 WH-UX12HE5 | WH-SXC12H6E5 WH-UX12HE5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 27.17 |  | 55 | 12.65 | 55 | 12.65 | WH-SXC12H6E5 WH-UX12HE5 | Heat pump |  | 29 | 6.27 | WH-SXC12H6E5_WH-UX12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC12H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1700 | 567 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-SXC12H6E5_WH-UX12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC12H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.271
HP_0720 | Panasonic | WH-SXC12H6E5 WH-UX12HE5 | WH-SXC12H6E5 WH-UX12HE5 | Heating only | Air Source | 1 | 230 |  |  | 27.17 |  | 55 | 12.65 | 55 | 12.65 | WH-SXC12H6E5 WH-UX12HE5 | Heat pump |  | 29 | 6.27 | WH-SXC12H6E5_WH-UX12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC12H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1650 | 550 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-SXC12H6E5_WH-UX12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SXC12H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.271
HP_0721 | Panasonic | WH-SDC12H6E5 WH-UD12HE5 | WH-SDC12H6E5 WH-UD12HE5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 18.57 |  | 50 | 11.5 | 50 | 11.5 | WH-SDC12H6E5 WH-UD12HE5 | Heat pump |  | 24 | 5.3 | WH-SDC12H6E5_WH-UD12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC12H6E5__TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1300 | 433 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-SDC12H6E5_WH-UD12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC12H6E5__TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.271
HP_0722 | Panasonic | WH-SDC12H6E5 WH-UD12HE5 | WH-SDC12H6E5 WH-UD12HE5 | Heating only | Air Source | 1 | 230 |  |  | 18.57 |  | 50 | 11.5 | 50 | 11.5 | WH-SDC12H6E5 WH-UD12HE5 | Heat pump |  | 24 | 5.3 | WH-SDC12H6E5_WH-UD12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC12H6E5__TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2200 | 733 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-SDC12H6E5_WH-UD12HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC12H6E5__TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.271
HP_0723 | Panasonic | WH-SDC16H6E5 WH-UD16HE5 | WH-SDC16H6E5 WH-UD16HE5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 21.5 |  | 52 | 11.96 | 52 | 11.96 | WH-SDC16H6E5 WH-UD162HE5 | Heat pump |  | 26 | 5.74 | WH-SDC16H6E5_WH-UD16HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC16H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1300 | 433 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-SDC16H6E5_WH-UD16HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC16H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.271
HP_0724 | Panasonic | WH-SDC16H6E5 WH-UD16HE5 | WH-SDC16H6E5 WH-UD16HE5 | Heating only | Air Source | 1 | 230 |  |  | 21.5 |  | 52 | 11.96 | 52 | 11.96 | WH-SDC16H6E5 WH-UD16HE5 | Heat pump |  | 24 | 5.3 | WH-SDC16H6E5_WH-UD16HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC16H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2200 | 733 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-SDC16H6E5_WH-UD16HE5_DoC | MRD-D17019-01 | EN 61000-3-12 | EN 61000-3-11 | WH-SDC16H6E5_TUEV,18008879_001,EMC-report | 18008879 001 | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.271
HP_0725 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0709J3E5 | WH-SDC0709J3E5 / WH-UD07JE5 | Heating only | Air Source | 1 | 230 |  |  | 19.73 |  | 28.9 | 6.65 | 28.9 | 6.65 | WH-SDC0709J3E5 / WH-UD07JE5 | Heat pump |  | 15.9 | 3.47 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21013_Harmonic Test Report -WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Heating) & SRFI-21015_Flicker Test Report - WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Heating) | SRFI-21013 & SRFI-21015 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0726 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0709J3E5 | WH-SDC0709J3E5 / WH-UD07JE5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 19.73 |  | 28.9 | 6.65 | 28.9 | 6.65 | WH-SDC0709J3E5 / WH-UD07JE5 | Heat pump |  | 15.9 | 3.47 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21014_Harmonic Test Report -WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Cooling) & SRFI-21016_Flicker Test Report - WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Cooling) | SRFI-21014 & SRFI-21016 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0727 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0709J3E5 | WH-SDC0709J3E5 / WH-UD09JE5 | Heating only | Air Source | 1 | 230 |  |  | 19.73 |  | 28.9 | 6.65 | 28.9 | 6.65 | WH-SDC0709J3E5 / WH-UD09JE5 | Heat pump |  | 15.9 | 3.47 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21013_Harmonic Test Report -WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Heating) & SRFI-21015_Flicker Test Report - WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Heating) | SRFI-21013 & SRFI-21015 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0728 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0709J3E5 | WH-SDC0709J3E5 / WH-UD09JE5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 19.73 |  | 28.9 | 6.65 | 28.9 | 6.65 | WH-SDC0709J3E5 / WH-UD09JE5 | Heat pump |  | 15.9 | 3.47 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21014_Harmonic Test Report -WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Cooling) & SRFI-21016_Flicker Test Report - WH-SDC0709J3E5;WH-UD09JE5-1 (Power Supply 1 Cooling) | SRFI-21014 & SRFI-21016 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0729 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0305J3E5 | WH-SDC0305J3E5/WH-UD05JE5 | Heating only | Air Source | 1 | 230 |  |  | 9.03 |  | 25 | 5.75 | 25 | 5.75 | WH-SDC0305J3E5/WH-UD05JE5 | Heat pump |  | 12 | 2.59 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21017_Harmonic Test Report - WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Heating) & SRFI-21019_Flicker Test Report -WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Heating) | SRFI-21017 & SRFI-21019 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0730 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0305J3E5 | WH-SDC0305J3E5/WH-UD05JE5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 9.03 |  | 25 | 5.75 | 25 | 5.75 | WH-SDC0305J3E5/WH-UD05JE5 | Heat pump |  | 12 | 2.59 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21018_Harmonic Test Report - WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Cooling) & SRFI-21020_Flicker Test Report -WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Cooling) | SRFI-21018 & SRFI-21020 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0731 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0305J3E5 | WH-SDC0305J3E5/WH-UD03JE5 | Heating only | Air Source | 1 | 230 |  |  | 9.03 |  | 25 | 5.75 | 25 | 5.75 | WH-SDC0305J3E5/WH-UD03JE5 | Heat pump |  | 12 | 2.59 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21017_Harmonic Test Report - WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Heating) & SRFI-21019_Flicker Test Report -WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Heating) | SRFI-21017 & SRFI-21019 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0732 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SDC0305J3E5 | WH-SDC0305J3E5/WH-UD03JE5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 9.03 |  | 25 | 5.75 | 25 | 5.75 | WH-SDC0305J3E5/WH-UD03JE5 | Heat pump |  | 12 | 2.59 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21018_Harmonic Test Report - WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Cooling) & SRFI-21020_Flicker Test Report -WH-SDC0305J3E5;WH-UD05JE5 (Power Supply 1 Cooling) | SRFI-21018 & SRFI-21020 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SDC0305_0709J3E5;WH-UD03,05,07,09JE5_09JE5-1,MRD-D18028-03,DoC | MRD-D18028-03 | EN 61000-3-2 | EN 61000-3-3 | SRFI-21022_Harmonic Test Report -Power Supply 2 Backup Heater & SRFI-21021_Flicker Test Report - Power Supply 2 Backup Heater | SRFI-21022 & SRFI-21021 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0733 | Panasonic | Mono-bloc Air-to-Water Heat Pump | WH-MHF12G6E5 | Heating only | Air Source | 1 | 230 |  |  | 23.58 |  | 55 | 12.65 | 55 | 12.65 | WH-MHF12G6E5 | Heat pump |  | 29 | 6.2 | WH-MHF12G6E5, MHF09G3E5, MRD-D15005-05,DoC | MRD-D15005-05 | EN 61000-3-12 | EN 61000-3-11 | 50274102 001_report | 50274102 001 | No | No | No | No | No | No | Yes | 50274102 001 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 1200 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-MHF12G6E5, MHF09G3E5, MRD-D15005-05,DoC | MRD-D15005-05 | EN 61000-3-12 | EN 61000-3-11 | 50274102 001_report | 50274102 001 | No | No | No | No | No | No | Yes | 50274102 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0734 | Panasonic | Mono-bloc Air-to-Water Heat Pump | WH-MHF09G3E5 | Heating only | Air Source | 1 | 230 |  |  | 21.86 |  | 41.5 | 9.55 | 41.5 | 9.55 | WH-MHF09G3E5 | Heat pump |  | 28.5 | 6.09 | WH-MHF12G6E5, MHF09G3E5, MRD-D15005-05,DoC | MRD-D15005-05 | EN 61000-3-12 | EN 61000-3-11 | 50274102 001_report | 50274102 001 | No | No | No | No | No | No | Yes | 50274102 001 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 1200 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MHF12G6E5, MHF09G3E5, MRD-D15005-05,DoC | MRD-D15005-05 | EN 61000-3-12 | EN 61000-3-11 | 50274102 001_report | 50274102 001 | No | No | No | No | No | No | Yes | 50274102 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.257
HP_0735 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SXC16H9E8 | WH-SXC16H9E8/ WH-UX16HE8 | Heating & Cooling | Air Source | 3 | 400 |  |  | 12.42 |  | 28.5 | 19.75 | 28.5 | 19.75 | WH-SXC16H9E8/ WH-UX16HE8 | Heat pump |  | 15.5 | 10.27 | WH-SQC09H3,SQC12,16H9E8,WH-UQ09,12,16HE8,MRD-D17020-04,DoC | MRD-D17020-04 | EN 61000-3-2 | EN 61000-3-11 | 18008880 001, EMC report | 18008880 001 | Yes | No | No | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
[17 empty] | Back-up heater - on-board |  | 13 | 9 | WH-SQC09H3,SQC12,16H9E8,WH-UQ09,12,16HE8,MRD-D17020-04,DoC | MRD-D17020-04 | EN 61000-3-2 | EN 61000-3-11 | 18008880 001, EMC report | 18008880 001 | Yes | No | No | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
HP_0736 | Panasonic | Bibloc Air-to-Water Heat Pump WH-SXC16H9E8 | WH-SXC16H9E8/ WH-UX16HE8 | Heating only | Air Source | 3 | 400 |  |  | 12.42 |  | 28.5 | 19.75 | 28.5 | 19.75 | WH-SXC16H9E8/ WH-UX16HE8 | Heat pump |  | 15.5 | 10.27 | WH-SQC09H3,SQC12,16H9E8,WH-UQ09,12,16HE8,MRD-D17020-04,DoC | MRD-D17020-04 | EN 61000-3-2 | EN 61000-3-11 | 18008880 001, EMC report | 18008880 001 | Yes | No | No | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 9 | WH-SQC09H3,SQC12,16H9E8,WH-UQ09,12,16HE8,MRD-D17020-04,DoC | MRD-D17020-04 | EN 61000-3-2 | EN 61000-3-11 | 18008880 001, EMC report | 18008880 001 | Yes | No | No | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_0737 | Panasonic | Bibloc Air-to-Water Heat Pump | WH-SHF09F3E5 / WH-UH09FE5 | Heating only | Air Source | 1 | 230 |  |  | 21.86 |  | 41.5 | 9.55 | 41.5 | 9.55 | WH-SHF09F3E5 / WH-UH09FE5 | Heat pump |  | 28.5 | 6.09 | WH-SHF09F3E5_WH-SHF12F6E5,WH-UH09_12FE5,MRD-D14005-06,DoC | MRD-D14005-6 | EN 61000-3-12 | EN 61000-3-11 | 50274100 001_report | 50274100 001 | No | No | No | No | No | No | Yes | 50274100 001 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 1100 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-SHF09F3E5_WH-SHF12F6E5,WH-UH09_12FE5,MRD-D14005-06,DoC | MRD-D14005-6 | EN 61000-3-12 | EN 61000-3-11 | 50274100 001_report | 50274100 001 | No | No | No | No | No | No | Yes | 50274100 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.244
HP_0738 | Panasonic | Air-to-Water Heat Pump | WH-SHF12F6E5 / WH-UH12FE5 | Heating only | Air Source | 1 | 230 |  |  | 23.58 |  | 55 | 12.65 | 55 | 12.65 | WH-SHF12F6E5 / WH-UH12FE5 | Heat pump |  | 29 | 6.2 | WH-SHF09F3E5_WH-SHF12F6E5,WH-UH09_12FE5,MRD-D14005-06,DoC | MRD-D14005-6 | EN 61000-3-12 | EN 61000-3-11 | 50274100 001_report | 50274100 001 | No | No | No | No | No | No | Yes | 50274100 001 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 1100 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 | WH-SHF09F3E5_WH-SHF12F6E5,WH-UH09_12FE5,MRD-D14005-06,DoC | MRD-D14005-6 | EN 61000-3-12 | EN 61000-3-11 | 50274100 001_report | 50274100 001 | No | No | No | No | No | No | Yes | 50274100 001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.244
HP_0739 | Panasonic | WH-MXC16H9E8 | WH-MXC16H9E8 | Heating & Cooling | Air Source | 3 | 400 |  |  | 12.42 |  | 28.5 | 19.75 | 28.5 | 19.75 | WH-MXC16H9E8 | Heat pump |  | 15.5 | 10.48 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-COC.pdf | AE 50468752 0001 | EN 61000-3-2 | EN 61000-3-3 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-report.pdf | 50274109 002 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 13 | 9 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-COC.pdf | AE 50468752 0001 | EN 61000-3-2 | EN 61000-3-3 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-report.pdf | 50274109 002 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0740 | Panasonic | WH-MXC16H9E8 | WH-MXC16H9E8 | Heating only | Air Source | 3 | 400 |  |  | 12.42 |  | 28.5 | 19.75 | 28.5 | 19.75 | WH-MXC16H9E8 | Heat pump |  | 15.5 | 10.48 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-COC.pdf | AE 50468752 0001 | EN 61000-3-2 | EN 61000-3-3 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-report.pdf | 50274109 002 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 13 | 9 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-COC.pdf | AE 50468752 0001 | EN 61000-3-2 | EN 61000-3-3 | WH-MXC09H3E8_MXC12,16H9E8,TUV,50274109 002,EMC-report.pdf | 50274109 002 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0741 | Panasonic | WH-MDC05J3E5 | WH-MDC05J3E5 | Heating only | Air Source | 1 | 230 |  |  | 11.75 |  | 25 | 5.75 | 25 | 5.75 | WH-MDC05J3E5 PS1 | Heat pump |  | 12 | 2.59 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-3 | WH-MDC05,07,09J3E5,TUV,MY21SC1Y 001,EMC-report.pdf | MY21SC1Y 001 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | WH-MDC05J3E5 PS2 | Back-up heater - on-board |  | 13 | 3 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-3 | WH-MDC05,07,09J3E5,TUV,MY21SC1Y 001,EMC-report.pdf | MY21SC1Y 001 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0742 | Panasonic | WH-MDC05J3E5 | WH-MDC05J3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 11.75 |  | 25 | 5.75 | 25 | 5.75 | WH-MDC05J3E5 PS1 | Heat pump |  | 12 | 2.59 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-3 | WH-MDC05,07,09J3E5,TUV,MY21SC1Y 001,EMC-report.pdf | MY21SC1Y 001 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | WH-MDC05J3E5 PS2 | Back-up heater - on-board |  | 13 | 3 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-3 | WH-MDC05,07,09J3E5,TUV,MY21SC1Y 001,EMC-report.pdf | MY21SC1Y 001 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0743 | Panasonic | WH-MDC07J3E5 | WH-MDC07J3E5 | Heating only | Air Source | 1 | 230 |  |  | 14.73 |  | 30 | 6.9 | 30 | 6.9 | WH-MDC07J3E5 | Heat pump |  | 17 | 3.83 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.10166 | 0.5203 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0744 | Panasonic | WH-MDC07J3E5 | WH-MDC07J3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 14.73 |  | 30 | 6.9 | 30 | 6.9 | WH-MDC07J3E5 | Heat pump |  | 17 | 3.83 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 32 | 0.12512 | 0.42279 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0745 | Panasonic | WH-MDC09J3E5 | WH-MDC09J3E5 | Heating only | Air Source | 1 | 230 |  |  | 16.91 |  | 30 | 6.9 | 30 | 6.9 | WH-MDC09J3E5 | Heat pump |  | 17 | 3.83 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.10166 | 0.5203 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0746 | Panasonic | WH-MDC09J3E5 | WH-MDC09J3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 16.91 |  | 30 | 6.9 | 30 | 6.9 | WH-MDC09J3E5 | Heat pump |  | 17 | 3.83 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 32 | 0.12512 | 0.42279 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 13 | 3 | WH-MDC05,07,09J3E5,MRD-D19008-02,DoC.pdf | MRD-D19008-02 | EN 61000-3-2 | EN 61000-3-11 | WH-MDC05,07,09J3E5_MY21SC1Y 003.pdf | MY21SC1Y 003 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_0747 | Panasonic | WH-MXC09J3E5 | WH-MXC09J3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 18.46 |  | 42 | 9.66 | 42 | 9.66 | WH-MXC09J3E5 | Heat pump |  | 29 | 6.27 | WH-MXC09J3E5,WH-MXC12J6E5,ACBD-D21001-02,DoC_01613029064 | ACBD-D21001-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC09J3E5,WH-MXC12J6E5,TUEV,50274108_002,EMC-report_1611223674.3942 | 50274108 002 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1900 | 633 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0748 | Panasonic | WH-MXC09J3E5 | WH-MXC09J3E5 | Heating only | Air Source | 1 | 230 |  |  | 18.46 |  | 42 | 9.66 | 42 | 9.66 | WH-MXC09J3E5 | Heat pump |  | 29 | 6.27 | WH-MXC09J3E5,WH-MXC12J6E5,ACBD-D21001-02,DoC_01613029064 | ACBD-D21001-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC09J3E5,WH-MXC12J6E5,TUEV,50274108_002,EMC-report_1611223674.3942 | 50274108 002 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1450 | 483 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0749 | Panasonic | WH-MXC12J6E5 | WH-MXC12J6E5 | Heating & Cooling | Air Source | 1 | 230 |  |  | 26.09 |  | 55 | 12.65 | 55 | 12.65 | WH-MXC12J6E5 | Heat pump |  | 29 | 6.27 | WH-MXC09J3E5,WH-MXC12J6E5,ACBD-D21001-02,DoC_01613029064 | ACBD-D21001-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC09J3E5,WH-MXC12J6E5,TUEV,50274108_002,EMC-report_1611223674.3942 | 50274108_002 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1900 | 633 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0750 | Panasonic | WH-MXC12J6E5 | WH-MXC12J6E5 | Heating only | Air Source | 1 | 230 |  |  | 26.09 |  | 55 | 12.65 | 55 | 12.65 | WH-MXC12J6E5 | Heat pump |  | 29 | 6.27 | WH-MXC09J3E5,WH-MXC12J6E5,ACBD-D21001-02,DoC_01613029064 | ACBD-D21001-02 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC09J3E5,WH-MXC12J6E5,TUEV,50274108_002,EMC-report_1611223674.3942 | 50274108_002 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1450 | 483 | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
[17 empty] | Back-up heater - on-board |  | 26 | 6 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.193
HP_0751 | Panasonic | CU-TZ20WKE + CS-TZ20WKEW | CU-TZ20WKE + CS-TZ20WKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 4.5 | 1.035 | 4.5 | 1.035 | CU-TZ20WKE + CS-TZ20WKEW | Whole system |  | 4.5 | 1.05 | CS-TZ20,25,35,42,50,60,71WKEW,CU-TZ20,25,35,42,50,60,71WKE,MRD-D19009-02,DoC_01629383815 | MRD-D19009-02 | EN 61000-3-2 | EN 61000-3-3 | CS-TZ20WKEW,CU-TZ20WKE,TUEV,50310551_001,EMC-report_1578919137.662 | 50310551 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-TZ20WKEW,CU-TZ20WKE,TUEV,50310551_001,EMC-report_1578919137.662 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0752 | Panasonic | CU-TZ25WKE + CS-TZ25WKEW | CU-TZ25WKE + CS-TZ25WKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 4.9 | 1.127 | 4.9 | 1.127 | CU-TZ25WKE + CS-TZ25WKEW | Whole system |  | 4.9 | 1.16 | CS-TZ20,25,35,42,50,60,71WKEW,CU-TZ20,25,35,42,50,60,71WKE,MRD-D19009-02,DoC_01629383815 | MRD-D19009-02 | EN 61000-3-2 | EN 61000-3-3 | CS-TZ25WKEW,CU-TZ25WKE,TUEV,50310571_001,EMC-report_1578919139.89 | 50310571 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-TZ25WKEW,CU-TZ25WKE,TUEV,50310571_001,EMC-report_1578919139.89 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0753 | Panasonic | CU-TZ35WKE + CS-TZ35WKEW | CU-TZ35WKE + CS-TZ35WKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 6.2 | 1.426 | 6.2 | 1.426 | CU-TZ35WKE + CS-TZ35WKEW | Whole system |  | 6.2 | 1.39 | CS-TZ20,25,35,42,50,60,71WKEW,CU-TZ20,25,35,42,50,60,71WKE,MRD-D19009-02,DoC_01629383815 | MRD-D19009-02 | EN 61000-3-2 | EN 61000-3-3 | CS-TZ35WKEW,CU-TZ35WKE,TUEV,50310574_001,EMC-report_1578919142.2079 | 50310574 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-TZ35WKEW,CU-TZ35WKE,TUEV,50310574_001,EMC-report_1578919142.2079 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0754 | Panasonic | CU-TZ42WKE + CS-TZ42WKEW | CU-TZ42WKE + CS-TZ42WKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 9 | 2.07 | 9 | 2.07 | CU-TZ42WKE + CS-TZ42WKEW | Whole system |  | 9 | 2.06 | CS-TZ20,25,35,42,50,60,71WKEW,CU-TZ20,25,35,42,50,60,71WKE,MRD-D19009-02,DoC_01629383815 | MRD-D19009-02 | EN 61000-3-2 | EN 61000-3-3 | CS-TZ42WKEW,CU-TZ42WKE,TUEV,50310575_001,EMC-report_1578919144.867 | 50310575 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-TZ42WKEW,CU-TZ42WKE,TUEV,50310575_001,EMC-report_1578919144.867 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0755 | Panasonic | CU-TZ50WKE + CS-TZ50WKEW | CU-TZ50WKE + CS-TZ50WKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.5 | 2.415 | 10.5 | 2.415 | CU-TZ50WKE + CS-TZ50WKEW | Whole system |  | 10.5 | 2.37 | CS-TZ20,25,35,42,50,60,71WKEW,CU-TZ20,25,35,42,50,60,71WKE,MRD-D19009-02,DoC_01629383815 | MRD-D19009-02 | EN 61000-3-2 | EN 61000-3-3 | CS-TZ50WKEW,CU-TZ50WKE,TUEV,50310576_001,EMC-report_1578919153.5828 | 50310576 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-TZ50WKEW,CU-TZ50WKE,TUEV,50310576_001,EMC-report_1578919153.5828 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0756 | Panasonic | CU-TZ60WKE + CS-TZ60WKEW | CU-TZ60WKE + CS-TZ60WKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.2 | 2.576 | 11.2 | 2.576 | CU-TZ60WKE + CS-TZ60WKEW | Whole system |  | 11.2 | 2.55 | CS-TZ20,25,35,42,50,60,71WKEW,CU-TZ20,25,35,42,50,60,71WKE,MRD-D19009-02,DoC_01629383815 | MRD-D19009-02 | EN 61000-3-2 | EN 61000-3-3 | CS-TZ60WKEW,CU-TZ60WKE,TUEV,50310578_001,EMC-report_1578919156.0333 | 50310578 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-TZ60WKEW,CU-TZ60WKE,TUEV,50310578_001,EMC-report_1578919156.0333 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0757 | Panasonic | CU-TZ71WKE + CS-TZ71WKEW | CU-TZ71WKE + CS-TZ71WKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.8 | 3.404 | 14.8 | 3.404 | CU-TZ71WKE + CS-TZ71WKEW | Whole system |  | 14.8 | 3.29 | CS-TZ20,25,35,42,50,60,71WKEW,CU-TZ20,25,35,42,50,60,71WKE,MRD-D19009-02,DoC_01629383815 | MRD-D19009-02 | EN 61000-3-2 | EN 61000-3-3 | CS-TZ71WKEW,CU-TZ71WKE,TUEV,50310579_001,EMC-report_1578919173.3176 | 50310579 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-TZ71WKEW,CU-TZ71WKE,TUEV,50310579_001,EMC-report_1578919173.3176 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0758 | Panasonic | CU-Z20XKE + CS-XZ20XKEW | CU-Z20XKE + CS-XZ20XKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 4.1 | 0.943 | 4.1 | 0.943 | CU-Z20XKE + CS-XZ20XKEW | Whole system |  | 4.1 | 1.03 | CS-Z20XKEW,CU-Z20XKE,CS-Z25XKEW,CU-Z25XKE,CS-XZ20XKEW,CS-XZ25XKEW,MRD-D20016-01,DoC_1609761762.6942 | MRD-D20016-01 | EN 61000-3-2 | EN 61000-3-3 | CS-Z20XKEW,CS-XZ20XKEW,CS-Z25XKEW,CU-Z20XKE,CU-Z25XKE,TUEV,NN20904N,EMC-report_1610537271.8614 | NN20904N | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z20XKEW,CS-XZ20XKEW,CS-Z25XKEW,CU-Z20XKE,CU-Z25XKE,TUEV,NN20904N,EMC-report_1610537271.8614 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0759 | Panasonic | CU-Z25XKE + CS-(X)Z25XKEW | CU-Z25XKE + CS-(X)Z25XKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 5.3 | 1.219 | 5.3 | 1.219 | CU-Z25XKE + CS-(X)Z25XKEW | Whole system |  | 5.3 | 1.28 | CS-Z20XKEW,CU-Z20XKE,CS-Z25XKEW,CU-Z25XKE,CS-XZ20XKEW,CS-XZ25XKEW,MRD-D20016-01,DoC_1609761762.6942 | MRD-D20016-01 | EN 61000-3-2 | EN 61000-3-3 | CS-Z20XKEW,CS-XZ20XKEW,CS-Z25XKEW,CU-Z20XKE,CU-Z25XKE,TUEV,NN20904N,EMC-report_1610537271.8614 | NN20904N | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z20XKEW,CS-XZ20XKEW,CS-Z25XKEW,CU-Z20XKE,CU-Z25XKE,TUEV,NN20904N,EMC-report_1610537271.8614 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0760 | Panasonic | CU-Z35XKE + CS-(X)Z35XKEW | CU-Z35XKE + CS-(X)Z35XKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 6.4 | 1.472 | 6.4 | 1.472 | CU-Z35XKE + CS-(X)Z35XKEW | Whole system |  | 6.4 | 1.54 | CS-Z35XKEW,CS-Z42XKEW,CS-XZ35XKEW,CU-Z35XKE,CU-Z42XKE,MRD-D20017-01,DoC_1609761764.9715 | MRD-D20017-01 | EN 61000-3-2 | EN 61000-3-3 | CS-Z35XKEW,CS-Z42XKEW,CS-XZ35XKEW,CU-Z35XKE,CU-Z42XKE,TUEV,MY20QQL0,EMC-report_1609927766.7206 | MY20QQL0 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z35XKEW,CS-Z42XKEW,CS-XZ35XKEW,CU-Z35XKE,CU-Z42XKE,TUEV,MY20QQL0,EMC-report_1609927766.7206 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0761 | Panasonic | CU-Z42XKE + CS-Z42XKEW | CU-Z42XKE + CS-Z42XKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 8.1 | 1.863 | 8.1 | 1.863 | CU-Z42XKE + CS-Z42XKEW | Whole system |  | 8.1 | 1.88 | CS-Z35XKEW,CS-Z42XKEW,CS-XZ35XKEW,CU-Z35XKE,CU-Z42XKE,MRD-D20017-01,DoC_1609761764.9715 | MRD-D20017-01 | EN 61000-3-2 | EN 61000-3-3 | CS-Z35XKEW,CS-Z42XKEW,CS-XZ35XKEW,CU-Z35XKE,CU-Z42XKE,TUEV,MY20QQL0,EMC-report_1609927766.7206 | MY20QQL0 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z35XKEW,CS-Z42XKEW,CS-XZ35XKEW,CU-Z35XKE,CU-Z42XKE,TUEV,MY20QQL0,EMC-report_1609927766.7206 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0762 | Panasonic | CU-Z50XKE + CS-(X)Z50XKEW | CU-Z50XKE + CS-(X)Z50XKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.5 | 2.415 | 10.5 | 2.415 | CU-Z50XKE + CS-(X)Z50XKEW | Whole system |  | 10.5 | 2.46 | CS-Z50XKEW,CS-Z71XKEW,CS-XZ50XKEW,CU-Z50XKE,CU-Z71XKE,MRD-D20018-01,DoC_1611301507.091 | MRD-D20018-01 | EN 61000-3-2 | EN 61000-3-3 | CS-Z50XKEW,CU-Z50XKE,TUEV,MY20X7L0,EMC-report_1611221665.1143 | MY20X7L0 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z50XKEW,CU-Z50XKE,TUEV,MY20X7L0,EMC-report_1611221665.1143 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0763 | Panasonic | CU-Z25UBEA + CS-Z25UFEAW | CU-Z25UBEA + CS-Z25UFEAW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 6.2 | 1.426 | 6.2 | 1.426 | CU-Z25UBEA + CS-Z25UFEAW | Whole system |  | 6.2 | 1.5 | CS-Z25_35_50UFEAW,CU-Z25_35_50UBEA,MRD-D17034-03,DoC_01564405314 | MRD-D17034-03 | EN 61000-3-2 | EN 61000-3-3 | CS-Z35_25UFEAW,CU-Z35_25UBEA,TUEV,18007278_001,EMC-report | 18007278 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z35_25UFEAW,CU-Z35_25UBEA,TUEV,18007278_001,EMC-report | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0764 | Panasonic | CU-Z35UBEA + CS-Z35UFEAW | CU-Z35UBEA + CS-Z35UFEAW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 8 | 1.84 | 8 | 1.84 | CU-Z35UBEA + CS-Z35UFEAW | Whole system |  | 8 | 1.82 | CS-Z25_35_50UFEAW,CU-Z25_35_50UBEA,MRD-D17034-03,DoC_01564405314 | MRD-D17034-03 | EN 61000-3-2 | EN 61000-3-3 | CS-Z35_25UFEAW,CU-Z35_25UBEA,TUEV,18007278_001,EMC-report | 18007278 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z35_25UFEAW,CU-Z35_25UBEA,TUEV,18007278_001,EMC-report | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0765 | Panasonic | CU-Z50UBEA + CS-Z50UFEAW | CU-Z50UBEA + CS-Z50UFEAW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.4 | 2.622 | 11.4 | 2.622 | CU-Z50UBEA + CS-Z50UFEAW | Whole system |  | 11.4 | 2.71 | CS-Z25_35_50UFEAW,CU-Z25_35_50UBEA,MRD-D17034-03,DoC_01564405314 | MRD-D17034-03 | EN 61000-3-2 | EN 61000-3-3 | CS-Z50UFEAW,CU-Z50UBEA,TUEV,18007277_001,EMC-report | 18007277 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z50UFEAW,CU-Z50UBEA,TUEV,18007277_001,EMC-report | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0766 | Panasonic | CU-Z25UBEA + CS-Z25UD3EAW | CU-Z25UBEA + CS-Z25UD3EAW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 5.6 | 1.288 | 5.6 | 1.288 | CU-Z25UBEA + CS-Z25UD3EAW | Whole system |  | 5.6 | 1.35 | CS-Z25,35,50,60UD3EAW,CU-Z25,35,50,60UBEA,MRD-D17025-03,DoC_01564402662 | MRD-D17025-03 | EN 61000-3-2 | EN 61000-3-3 | CS-Z25,35UD3EAW,CU-Z25,35UBEA,TUEV,18007169_001,EMC-report | 18007169 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z25,35UD3EAW,CU-Z25,35UBEA,TUEV,18007169_001,EMC-report | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0767 | Panasonic | CU-Z35UBEA + CS-Z35UD3EAW | CU-Z35UBEA + CS-Z35UD3EAW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 6.6 | 1.518 | 6.6 | 1.518 | CU-Z35UBEA + CS-Z35UD3EAW | Whole system |  | 6.6 | 1.46 | CS-Z25,35,50,60UD3EAW,CU-Z25,35,50,60UBEA,MRD-D17025-03,DoC_01564402662 | MRD-D17025-03 | EN 61000-3-2 | EN 61000-3-3 | CS-Z25,35UD3EAW,CU-Z25,35UBEA,TUEV,18007169_001,EMC-report | 18007169 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z25,35UD3EAW,CU-Z25,35UBEA,TUEV,18007169_001,EMC-report | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0768 | Panasonic | CU-Z50UBEA + CS-Z50UD3EAW | CU-Z50UBEA + CS-Z50UD3EAW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 9.9 | 2.277 | 9.9 | 2.277 | CU-Z50UBEA + CS-Z50UD3EAW | Whole system |  | 9.9 | 2.25 | CS-Z25,35,50,60UD3EAW,CU-Z25,35,50,60UBEA,MRD-D17025-03,DoC_01564402662 | MRD-D17025-03 | EN 61000-3-2 | EN 61000-3-3 | CS-Z50,60UD3EAW,CU-Z50,60UBEA,TUEV,18007181_001,EMC-report | 18007181 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z50,60UD3EAW,CU-Z50,60UBEA,TUEV,18007181_001,EMC-report | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0769 | Panasonic | CU-Z60UBEA + CS-Z60UD3EAW | CU-Z60UBEA + CS-Z60UD3EAW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 12.3 | 2.829 | 12.3 | 2.829 | CU-Z60UBEA + CS-Z60UD3EAW | Whole system |  | 12.3 | 2.78 | CS-Z25,35,50,60UD3EAW,CU-Z25,35,50,60UBEA,MRD-D17025-03,DoC_01564402662 | MRD-D17025-03 | EN 61000-3-2 | EN 61000-3-3 | CS-Z50,60UD3EAW,CU-Z50,60UBEA,TUEV,18007181_001,EMC-report | 18007181 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z50,60UD3EAW,CU-Z50,60UBEA,TUEV,18007181_001,EMC-report | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0770 | Panasonic | CU-Z71XKE + CS-(X)Z71XKEW | CU-Z71XKE + CS-(X)Z71XKEW | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.6 | 3.588 | 15.6 | 3.588 | CU-Z71XKE + CS-(X)Z71XKEW | Whole system |  | 15.6 | 3.49 | CS-Z50XKEW,CS-Z71XKEW,CS-XZ50XKEW,CU-Z50XKE,CU-Z71XKE,MRD-D20018-01,DoC_1611301507.091 | MRD-D20018-01 | EN 61000-3-2 | EN 61000-3-3 | CS-Z71XKEW,CU-Z71XKE,TUEV,MY20D5E7,EMC-report_1611221673.5529 | MY20D5E7 | Yes | Yes | Yes | Yes | Yes | Yes | No | CS-Z71XKEW,CU-Z71XKE,TUEV,MY20D5E7,EMC-report_1611221673.5529 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0771 | Panasonic | PACi NX Standard | U-25PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 8.9 | 2.052 | 8.9 | 2.052 | U-25PZ3E5 | Heat pump |  | 8.9 | 2.052 | U-25PZ3E5,U-36PZ3E5,MRD-D20024-01,DoC_1611308348.3854 | MRD-D20024-01 | EN 61000-3-2 | EN 61000-3-3 | U-25PZ3E5,U-36PZ3E5,TUEV,60414635_001,EMC-report_1611650519.5635 | 60414635 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-25PZ3E5,U-36PZ3E5,TUEV,60414635_001,EMC-report_1611650519.5635 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0772 | Panasonic | PACi NX Standard | U-36PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 8.9 | 2.052 | 8.9 | 2.052 | U-36PZ3E5 | Heat pump |  | 8.9 | 2.052 | U-25PZ3E5,U-36PZ3E5,MRD-D20024-01,DoC_1611308348.3854 | MRD-D20024-01 | EN 61000-3-2 | EN 61000-3-3 | U-25PZ3E5,U-36PZ3E5,TUEV,60414635_001,EMC-report_1611650519.5635 | 60414635 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-25PZ3E5,U-36PZ3E5,TUEV,60414635_001,EMC-report_1611650519.5635 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0773 | Panasonic | PACi NX Standard | U-50PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.5 | 2.42 | 10.5 | 2.42 | U-50PZ3E5 | Heat pump |  | 10.5 | 2.42 | U-50PZ3E5,MRD-D20026-01,DoC_1611308339.5232 | MRD-D20026-01 | EN 61000-3-2 | EN 61000-3-3 | U-50PZ3E5,TUEV,MY206M6N_001,EMC-report_1611650675.0276 | MY206M6N 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-50PZ3E5,TUEV,MY206M6N_001,EMC-report_1611650675.0276 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0774 | Panasonic | PACi NX Standard | U-60PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13.1 | 3.013 | 13.1 | 3.013 | U-60PZ3E5 | Heat pump |  | 13.1 | 2.705 | U-60PZ3E5A,U-71PZ3E5A,MRD-D20025-01,DoC_1611308345.0099 | MRD-D20025-01 | EN 61000-3-2 | EN 61000-3-3 | U-60PZ3E5A,TUEV,MY20FD8L_001,EMC-report_1611650731.1726 | MY20FD8L 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-60PZ3E5A,TUEV,MY20FD8L_001,EMC-report_1611650731.1726 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0775 | Panasonic | PACi NX Standard | U-71PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.8 | 3.404 | 14.8 | 3.404 | U-71PZ3E5 | Heat pump |  | 14.8 | 3.184 | U-60PZ3E5A,U-71PZ3E5A,MRD-D20025-01,DoC_1611308345.0099 | MRD-D20025-01 | EN 61000-3-2 | EN 61000-3-3 | U-71PZ3E5A,TUEV,MY206LT5_001,EMC-report_1611650746.3338 | MY206LT5 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-71PZ3E5A,TUEV,MY206LT5_001,EMC-report_1611650746.3338 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0776 | Panasonic | PACI NX Elite | U-36PZH3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11 | 2.53 | 11 | 2.53 | U-36PZH3E5 | Heat pump |  | 11 | 2.5 | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,MRD-D20014-02,DoC_01611308412 | MRD-D20014-02 | EN 61000-3-12 | EN 61000-3-11 | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,TUEV,60406798_001,EMC-report_1606813676.3261 | 60406798 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,TUEV,60406798_001,EMC-report_1606813676.3261 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0777 | Panasonic | PACI NX Elite | U-50PZH3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 12 | 2.76 | 12 | 2.76 | U-50PZH3E5 | Heat pump |  | 12 | 2.68 | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,MRD-D20014-02,DoC_01611308412 | MRD-D20014-02 | EN 61000-3-12 | EN 61000-3-11 | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,TUEV,60406798_001,EMC-report_1606813676.3261 | 60406798 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,TUEV,60406798_001,EMC-report_1606813676.3261 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0778 | Panasonic | PACI NX Elite | U-60PZH3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.4 | 3.772 | 16.4 | 3.772 | U-60PZH3E5 | Heat pump |  | 16.4 | 3.65 | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,MRD-D20014-02,DoC_01611308412 | MRD-D20014-02 | EN 61000-3-12 | EN 61000-3-11 | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,TUEV,60406798_001,EMC-report_1606813676.3261 | 60406798 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-36PZH3E5,U-50PZH3E5,U-60PZH3E5,TUEV,60406798_001,EMC-report_1606813676.3261 | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0779 | Panasonic | PACi NX Standard | U-100PZ3E8 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 11.9 | 8.2446 | 11.9 | 8.2446 | U-100PZ3E8 | Heat pump |  | 11.9 | 6.913 | U-100PZ3E8,MRD-D20006-01,EMC-DoC_1589285553.5499 | MRD-D20006-01 | EN 61000-3-2 | EN 61000-3-3 | U-100PZ3E8,TUEV,50341127_001,EMC-report_1589288714.2129 | 50341127 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-100PZ3E8,TUEV,50341127_001,EMC-report_1589288714.2129 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0780 | Panasonic | PACi NX Standard | U-125PZ3E8 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 12.9 | 8.9374 | 12.9 | 8.9374 | U-125PZ3E8 | Heat pump |  | 12.9 | 7.38 | U-125PZ3E8,U-140PZ3E8,MRD-D20007-01,EMC-DoC_1589285559.2695 | MRD-D20007-01 | EN 61000-3-2 | EN 61000-3-3 | U-125PZ3E8,U-140PZ3E8,TUEV,50361644_001,EMC-report_1589288892.0287 | 50361644 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-125PZ3E8,U-140PZ3E8,TUEV,50361644_001,EMC-report_1589288892.0287 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0781 | Panasonic | PACi NX Standard | U-140PZ3E8 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13.4 | 9.2838 | 13.4 | 9.2838 | U-140PZ3E8 | Heat pump |  | 13.4 | 7.756 | U-125PZ3E8,U-140PZ3E8,MRD-D20007-01,EMC-DoC_1589285559.2695 | MRD-D20007-01 | EN 61000-3-2 | EN 61000-3-3 | U-125PZ3E8,U-140PZ3E8,TUEV,50361644_001,EMC-report_1589288892.0287 | 50361644 001 | Yes | Yes | Yes | Yes | Yes | Yes | No | U-125PZ3E8,U-140PZ3E8,TUEV,50361644_001,EMC-report_1589288892.0287 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0782 | Panasonic | PACi NX Standard | U-100PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.9 | 6.417 | 27.9 | 6.417 | U-100PZ3E5 | Heat pump |  | 27.9 | 6.53 | U-100PZ3E5,U-125PZ3E5,U-140PZ3E5,MRD-D20004-03,DoC_01611308885.pdf | MRD-D20004-03 | EN 61000-3-12 | EN 61000-3-11 | U-100PZ3E5,MRD-D20002-01,EMC-DoC_1589285548.2459.pdf | MRD-D20002-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 1718 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0783 | Panasonic | KIT-BZ25-XKE | CU-BZ25XKE - CS-BZ25XKE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 4.8 | 1.104 | 4.8 | 1.104 | CU-BZ25XKE - CS-BZ25XKE | Whole system |  | 4.8 | 1.08 | CU-BZ25XKE,CU-BZ35XKE,MRD-D21021-01,DoC_1640094689.7709 | MRD-D21021-01 | EN 61000-3-2 | EN 61000-3-3 | CU-BZ25XKE,TUV,50310551 004,EMC-report_1640096025.1643 | 50310551 004 | Yes | Yes | Yes | Yes | Yes | Yes | No | CU-BZ25XKE,TUV,50310551 004,EMC-report_1640096025.1643 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0784 | Panasonic | KIT-BZ35-XKE | CU-BZ35XKE - CS-BZ35XKE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 7 | 1.61 | 7 | 1.61 | CU-BZ35XKE - CS-BZ35XKE | Whole system |  | 7 | 1.61 | CU-BZ25XKE,CU-BZ35XKE,MRD-D21021-01,DoC_1640094689.7709 | MRD-D21021-01 | EN 61000-3-2 | EN 61000-3-3 | CU-BZ35XKE,TUV,50310571 003,EMC-report_1640096029.6121 | 50310571 003 | Yes | Yes | Yes | Yes | Yes | Yes | No | CU-BZ35XKE,TUV,50310571 003,EMC-report_1640096029.6121 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0785 | Panasonic | KIT-BZ50-XKE | CU-BZ50XKE - CS-BZ50XKE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.8 | 2.484 | 10.8 | 2.484 | CU-BZ50XKE - CS-BZ50XKE | Whole system |  | 10.8 | 2.53 | CU-BZ50XKE,CU-BZ60XKE,MRD-D21022-01,DoC_1640094687.8388 | MRD-D21022-01 | EN 61000-3-2 | EN 61000-3-3 | CU-BZ50XKE,TUV,50310576 003,EMC-report_1640096077.4316 | 50310576 003 | Yes | Yes | Yes | Yes | Yes | Yes | No | CU-BZ50XKE,TUV,50310576 003,EMC-report_1640096077.4316 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0786 | Panasonic | KIT-BZ60-XKE | CU-BZ60XKE - CS-BZ60XKE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.9 | 2.737 | 11.9 | 2.737 | CU-BZ60XKE - CS-BZ60XKE | Whole system |  | 11.9 | 2.73 | CU-BZ50XKE,CU-BZ60XKE,MRD-D21022-01,DoC_1640094687.8388 | MRD-D21022-01 | EN 61000-3-2 | EN 61000-3-3 | CU-BZ60XKE,TUV,50310593 002,EMC-report_1640096080.6313 | 50310593 002 | Yes | Yes | Yes | Yes | Yes | Yes | No | CU-BZ60XKE,TUV,50310593 002,EMC-report_1640096080.6313 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0787 | Panasonic | PACi NX Standard | U-125PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 32.9 | 7.57 | 32.9 | 7.57 | U-125PZ3E5 | Heat pump |  | 32.9 | 7.57 | U-125PZ3E5,U-140PZ3E5,MRD-D20003-01,EMC-DoC_1589285557.7115.pdf | MRD-D20003-01 | EN 61000-3-12 | EN 61000-3-11 | U-125PZ3E5,U-140PZ3E5,TUEV,50361815_001,EMC-report_1589288886.1547.pdf | 50361815 001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 1892 | N/A | N/A | N/A | Not applicable
HP_0788 | Panasonic | PACi NX Standard | U-140PZ3E5 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 32.9 | 7.57 | 32.9 | 7.57 | U-140PZ3E5 | Heat pump |  | 32.9 | 7.57 | U-125PZ3E5,U-140PZ3E5,MRD-D20003-01,EMC-DoC_1589285557.7115.pdf | MRD-D20003-01 | EN 61000-3-12 | EN 61000-3-11 | U-125PZ3E5,U-140PZ3E5,TUEV,50361815_001,EMC-report_1589288886.1547.pdf | 50361815 001 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 1892 | N/A | N/A | N/A | Not applicable
HP_0789 | Panasonic | WH-MXC12J9E8 | WH-MXC12J9E8 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | WH-MXC12J9E8 | Heat pump |  | 13 | 9 | WH-MXC09J3E8,WH-MXC12J9E8,WH-MXC16J9E8,ACBD-D21003-03,DoC | ACBD-D21003-03 | EN 61000-3-2 | EN 61000-3-3 | WH-MXC12J9E8,S21006-E,EMC-report | S21006-E | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0790 | Panasonic | WH-MXC12J9E8 | WH-MXC12J9E8 | Heating only | Air Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | WH-MXC12J9E8 | Heat pump |  | 13 | 9 | WH-MXC09J3E8,WH-MXC12J9E8,WH-MXC16J9E8,ACBD-D21003-03,DoC | ACBD-D21003-03 | EN 61000-3-2 | EN 61000-3-3 | WH-MXC12J9E8,S21006-E,EMC-report | S21006-E | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0791 | Panasonic | WH-MXC16J9E8 | WH-MXC16J9E8 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 29.4 | 20.37 | 29.4 | 20.37 | WH-MXC16J9E8 | Heat pump |  | 16.4 | 11.36 | WH-MXC09J3E8,WH-MXC12J9E8,WH-MXC16J9E8,ACBD-D21003-03,DoC | ACBD-D21003-03 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC16J9E8,S21008-E,EMC-report | S21008-E | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 546 |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0792 | Panasonic | WH-MXC16J9E8 | WH-MXC16J9E8 | Heating only | Air Source | 3 | 400 |  |  |  |  | 29.4 | 20.37 | 29.4 | 20.37 | WH-MXC16J9E8 | Heat pump |  | 16.4 | 11.36 | WH-MXC09J3E8,WH-MXC12J9E8,WH-MXC16J9E8,ACBD-D21003-03,DoC | ACBD-D21003-03 | EN 61000-3-12 | EN 61000-3-11 | WH-MXC16J9E8,S21008-E,EMC-report | S21008-E | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0793 | Panasonic | PACi NX Elite | U-71PZH3E8 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 6.7 | 4.64 | 6.7 | 4.64 | U-71PZH3E8 | Heat pump |  | 6.7 | 4.78 | U-71PZH3E8,U-100PZH3E8,U-125PZH3E8,U-140PZH3E8,ACBD-D20E02-01,DoC_1651493382.5099 | ACBD-D20E02-01 | EN 61000-3-2 | EN 61000-3-3 | S20002-E | S20002-E-a | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A
HP_0803 | M-Tec international | ECOAir | WPL412 230V | Heating only | Air Source | 1 | 230 |  |  |  |  | 3.91 | 0.9 | 6.72 | 1.55 | WPL412 230V | Whole system |  | 6.72 | 1.55 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0804 | M-Tec international | ECOAir | WPL618 230V | Heating only | Air Source | 1 | 230 |  |  |  |  | 6.09 | 1.4 | 10.12 | 2.34 | WPL618 230V | Whole system |  | 10.12 | 2.34 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0805 | M-Tec international | ECOAir | WPLC412 230V | Heating only | Air Source | 1 | 230 |  |  |  |  | 3.91 | 0.9 | 6.45 | 1.48 | WPLC412 230V | Heat pump |  | 3.91 | 0.9 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0806 | M-Tec international | UrbanECO | WPS26 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 2.61 | 0.6 | 4.24 | 0.98 | WPS26 | Heat pump |  | 2.61 | 0.6 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0807 | M-Tec international | RuralECO | WPS618 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 4.35 | 1 | 8.4 | 1.93 | WPS618 | Heat pump |  | 4.35 | 1 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0808 | M-Tec international | UrbanECO | WPS-W26 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 3.04 | 0.7 | 4.36 | 1 | WPS-W26 230V | Heat pump |  | 3.04 | 0.7 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0809 | M-Tec international | UrbanECO | WPS-W412 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 2.61 | 0.6 | 4.61 | 1.06 | WPS-W412 230V | Heat pump |  | 2.61 | 0.6 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0810 | M-Tec international | UrbanECO | WPS-W618 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 3.91 | 0.9 | 8.23 | 1.9 | WPS-W618 230V | Heat pump |  | 3.91 | 0.9 | 20190409_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200326_PicoEnergy HPs_EN61000 Confrmation_signed | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0811 | M-Tec international | WPS1052 AC 400V | WPS1052 AC 400V | Heating & Cooling | Ground Source | 3 | 400 |  |  |  |  | 7.61 | 5.27 | 8.2 | 5.68 | WPS1052 AC 400V | Heat pump |  | 7.61 | 5.27 | 20200902_EC Declaration of Conformity |  | EN 61000-3-2 | EN 61000-3-3 | 20200902_WPS1052 AC 400V EN61000 Confirmation |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 20200902_WPS1052 AC 400V EN61000 Confrmation | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_0901 | Samsung | AE090JXYDEH | AE090JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | AE090JXYDEH | Heat pump |  | 22 | 5.06 | 1584.CE DoC_AE090JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | CEC2014-0236-TEST.pdf | CEC2014-0236 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.0886 | 0.59698 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No
HP_0902 | Samsung | AE120JXYDEH | AE120JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE120JXYDEH | Heat pump |  | 32 | 7.36 | 1585.CE DoC_AE160JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 12 14 16 kW CEC2014-0237_성적서.pdf | CEC2014-0237 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 11 | 0.08096 | 0.65341 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No
HP_0903 | Samsung | AE140JXYDEH | AE140JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE140JXYDEH | Heat pump |  | 32 | 7.36 | 1585.CE DoC_AE160JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 12 14 16 kW CEC2014-0237_성적서.pdf | CEC2014-0237 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 11 | 0.08096 | 0.65341 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No
HP_0904 | Samsung | AE160JXYDEH | AE160JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE160JXYDEH | Heat pump |  | 32 | 7.36 | 1585.CE DoC_AE160JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 12 14 16 kW CEC2014-0237_성적서.pdf | CEC2014-0237 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 11 | 0.08096 | 0.65341 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No
HP_0905 | Samsung | AE050JXYDEH | AE050JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 20 | 4.6 | 20 | 4.6 | AE050JXYDEH | Heat pump |  | 20 | 4.9 | 1583.CE DoC_AE050JXYDEH_150603_Rev00.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 5kW CEC2014-0235_성적서.pdf | CEC2014-0235 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No
HP_0906 | Samsung | AE050RXYDEG/EU | AE050RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  | 12.65 |  | 16 | 3.68 | 16 | 3.68 | AE050RXYDEG/EU | Whole system |  | 16 | 3.68 | 19032_CE DoC AE050RXYDEG_Rev00 |  | EN 61000-3-2 | EN 61000-3-3 | ECE-2019-000022_Rv1 | ECE-2019-000022 | Yes | Yes | Yes | Yes | Yes | Yes | No | 1.SSEC_EHS_R-32_OUT_MONO_EU_IM_DB68-08368A-00_EN_20190409 | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No |  | Yes | No |  | Yes | No
HP_0907 | Samsung | AE080RXYDEG/EU | AE080RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  | 17.43 |  | 22 | 5.06 | 22 | 5.06 | AE080RXYDEG/EU | Whole system |  | 22 | 5.06 | 19033_CE DoC AE080RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000023_Rv1 | ECE-2019-000023 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No |  | Yes | No |  | Yes | No
HP_0908 | Samsung | AE120RXYDEG/EU | AE120RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  | 29.74 |  | 28 | 6.44 | 28 | 6.44 | AE120RXYDEG/EU | Whole system |  | 28 | 6.44 | 19035_CE DoC AE160RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000024_Rv1 | ECE-2019-000024 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No |  | Yes | No |  | Yes | No
HP_0909 | Samsung | AE160RXYDEG/EU | AE160RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  | 35.09 |  | 32 | 7.36 | 32 | 7.36 | AE160RXYDEG/EU | Whole system |  | 32 | 7.36 | 19035_CE DoC AE160RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000024_Rv1 | ECE-2019-000024 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No |  | Yes | No |  | Yes | No
HP_0910 | Samsung | AE090JXYDEH | AE090JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | AE090JXYDEH | Heat pump |  | 22 | 5.06 | 1584.CE DoC_AE090JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | CEC2014-0236-TEST.pdf | CEC2014-0236 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.0886 | 0.59698 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0911 | Samsung | AE120JXYDEH | AE120JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE120JXYDEH | Heat pump |  | 32 | 7.36 | 1585.CE DoC_AE160JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 12 14 16 kW CEC2014-0237_성적서.pdf | CEC2014-0237 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 11 | 0.08096 | 0.65341 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0912 | Samsung | AE140JXYDEH | AE140JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE140JXYDEH | Heat pump |  | 32 | 7.36 | 1585.CE DoC_AE160JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 12 14 16 kW CEC2014-0237_성적서.pdf | CEC2014-0237 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 11 | 0.08096 | 0.65341 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0913 | Samsung | AE160JXYDEH | AE160JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE160JXYDEH | Heat pump |  | 32 | 7.36 | 1585.CE DoC_AE160JXYDEH_150227_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 12 14 16 kW CEC2014-0237_성적서.pdf | CEC2014-0237 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 11 | 0.08096 | 0.65341 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0914 | Samsung | AE050JXYDEH | AE050JXYDEH | Heating only | Air Source | 1 | 230 |  |  |  |  | 20 | 4.6 | 20 | 4.6 | AE050JXYDEH | Heat pump |  | 20 | 4.6 | 1583.CE DoC_AE050JXYDEH_150603_Rev00.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 5kW CEC2014-0235_성적서.pdf | CEC2014-0235 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0915 | Samsung | AE050RXYDEG/EU | AE050RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | AE050RXYDEG/EU | Heat pump |  | 16 | 3.68 | 19032_CE DoC AE050RXYDEG_Rev00 |  | EN 61000-3-2 | EN 61000-3-3 | ECE-2019-000022_Rv1 | ECE-2019-000022 | Yes | Yes | Yes | Yes | Yes | Yes | No | 1.SSEC_EHS_R-32_OUT_MONO_EU_IM_DB68-08368A-00_EN_20190409 | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0916 | Samsung | AE080RXYDEG/EU | AE080RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | AE080RXYDEG/EU | Heat pump |  | 22 | 5.06 | 19033_CE DoC AE080RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000023_Rv1 | ECE-2019-000023 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0917 | Samsung | AE120RXYDEG/EU | AE120RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  |  |  | 28 | 6.44 | 28 | 6.44 | AE120RXYDEG/EU | Heat pump |  | 28 | 6.44 | 19035_CE DoC AE160RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000024_Rv1 | ECE-2019-000024 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0918 | Samsung | AE160RXYDEG/EU | AE160RXYDEG/EU | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE160RXYDEG/EU | Heat pump |  | 32 | 7.36 | 19035_CE DoC AE160RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000024_Rv1 | ECE-2019-000024 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_0919 | Samsung | AE080BXYDEG | AE080BXYDEG | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24 | 5.52 | 24 | 5.52 | AE080BXYDEG | Heat pump |  | 24 | 5.52 | 22037_CE+DoC+AE140BXYDEG_Rev00(Multilingual)_Rev00 (1) |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2022-000111 AE140BXYDEG.pdf | ECE-2022-000111 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.125 | 0.423 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0920 | Samsung | AE120BXYDEG | AE120BXYDEG | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE120BXYDEG | Heat pump |  | 32 | 7.36 | 22037_CE+DoC+AE140BXYDEG_Rev00(Multilingual)_Rev00 (1) |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2022-000111 AE140BXYDEG.pdf | ECE-2022-000111 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.125 | 0.423 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0921 | Samsung | AE140BXYDEG | AE140BXYDEG | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | AE140BXYDEG | Heat pump |  | 32 | 7.36 | 22037_CE+DoC+AE140BXYDEG_Rev00(Multilingual)_Rev00 (1) |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2022-000111 AE140BXYDEG.pdf | ECE-2022-000111 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.125 | 0.423 | Equipment complying with IEC 61000-3-3 technical requirements
HP_0922 | Samsung | AE160RXYDGG | AE160RXYDGG | Heating only | Air Source | 3 | 400 |  |  |  |  | 16.1 | 11.15 | 16.1 | 11.15 | AE160RXYDGG | Heat pump |  | 16.1 | 11.15 | AE160RXYDDG |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000026 AE160RXYDGG (002) | ECE-2019-000026 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2253 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_1001 | Stiebel Eltron | WPF 13 S | 232925 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 40 | 9.2 | 40 | 9.2 | 232925 | Heat pump | 4017212329252 | 11.91 | 2.74 | WPF (S) - CE.pdf | D0000045852b | EN 61000-3-12 | EN 61000-3-11 |  |  | No | No | No | No | No | No | Yes | Electrical information for J2 forms.xlsx | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.345
[17 empty] | Back-up heater |  | 13.04 | 3 | [6 empty] | No | No | No |  |  |  | Yes | Electrical information for J2 forms.xlsx | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.345
[17 empty] | Boost heater |  | 13.04 | 3 | [6 empty] | No | Yes | No |  |  |  | Yes | Electrical information for J2 forms.xlsx |  |  |  | N/A | N/A | N/A
HP_1002 | Stiebel Eltron | WPL 25 AS + 6.2kW heating element | 236642 | Heating only | Air Source | 1 | 230 | 18.76 |  |  |  | 37 | 8.51 | 63.9565 | 14.71 | 236642 | Whole system | 4017212366424 | 37 | 8.51 | WPL (All) - CE - 2019 & EMC_WPL_25_AS | D0000069994-d & D0000048147-a | EN 61000-3-12 | EN 61000-3-11 | D0000048147-a_emc_wpl_25_as | Testreport-EC1-1-194267.docx | Yes | No | No | No | No | No | Yes | D0000069994-d & D0000048147-a_emc_wpl_25_as | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.214 | No |  |  | No |  |  | No
HP_1003 | Stiebel Eltron | WPL 25 AS + 3kW heating element | 236642 | Heating only | Air Source | 1 | 230 | 18.76 |  |  |  | 37 | 8.51 | 50.04 | 11.51 | 236642 | Whole system | 4017212366424 | 37 | 8.51 | WPL (All) - CE - 2019 & EMC_WPL_25_AS | D0000069994-d & D0000048147-a | EN 61000-3-12 | EN 61000-3-11 | D0000048147-a_emc_wpl_25_as | Testreport-EC1-1-194267.docx | Yes | Yes | Yes | Yes | No | No | Yes | D0000069994-d & D0000048147-a_emc_wpl_25_as | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1004 | Stiebel Eltron | WPL 17 ACS Classic + 3kW heating element | 235922 | Heating only | Air Source | 1 | 230 | 11.61 |  |  |  | 14 | 3.22 | 27.0435 | 6.22 | 235922 | Whole system | 4017212359228 | 27.0435 | 6.22 | D0000069994-h.docx | 235922 WPL 17 ACS classic D0000069994-h.docx | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 236376 (WPL 17 ICS classic 9234-0 emf) | 235922 (WPL 17 ACS Classic 9134-0) | No | Yes | No | No | Yes | No | Yes | 235922 (WPL 17 ACS Classic 9134-0) | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1005 | Stiebel Eltron | WPL 15 AS + 3kW Heating Element | 236638 | Heating only | Air Source | 1 | 230 |  |  |  |  | 34.35 | 7.9 | 34.35 | 7.9 | 236638 | Whole system |  | 34.35 | 7.9 | WPL (All) - CE - 2019 | WPL (All) - CE - 2019 / D0000069994-d | EN 61000-3-12 | EN 61000-3-11 | WPL 15 AS & ACS EMC Test Report | 244172-TL7-1 | No | Yes | No | No | No | No | Yes | 244172-TL7-1 | Equipment complying with IEC 61000-3-12 |  |  | 15 | 0.073485 | 0.72 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1006 | Stiebel Eltron | WPL 15 AS + 6.2kW Heating Element | 236638 | Heating only | Air Source | 1 | 230 |  |  |  |  | 48.26 | 11.1 | 48.26 | 11.1 | 236638 | Whole system |  | 48.26 | 11.1 | WPL (All) - CE - 2019 | WPL (All) - CE - 2019 / D0000069994-d | EN 61000-3-12 | EN 61000-3-11 | WPL 15 AS & ACS EMC Test Report | 244172-TL7-1 | No | Yes | No | No | No | No | Yes | 244172-TL7-1 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1007 | Stiebel Eltron | WPL 17 ACS + 5.9kW Heating Element | 235922 | Heating only | Air Source | 1 | 230 |  |  |  |  | 39.65 | 9.12 | 39.65 | 9.12 | 235922 | Whole system | 4017212359228 | 39.65 | 9.12 | D0000069994 EU Conformity | D0000069994-h.docx | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 236376 (WPL 17 ICS classic 9234-0 emf) + WPL 15 AS & ACS EMC Test Report | 235922 (WPL 17 ACS Classic 9134-0) + 244172-TL7-1 | No | No | No | No | No | No | Yes | 235922 (WPL 17 ACS Classic 9134-0) + 244172-TL7-1 | Equipment complying with IEC 61000-3-12 |  |  | 9 | 0.03933 | 1.345 | Requires Zsource ≤Zmax | 0.2122 | No |  |  | No |  |  | No
HP_1008 | Stiebel Eltron | WPE-I 87 H 400 Premium | WPE-I 87 H 400 Premium | Heating only | Ground Source | 3 | 400 |  |  |  |  | 54.2 | 37.55 | 54.2 | 37.55 | WPE-I 87 H 400 Premium | Heat pump |  | 54.2 | 37.55 | D0000086451-a.pdf | AO857/07.2018 | EN 61000-3-12 | EN 61000-3-11 | 1511389STO-001, Ed2.pdf | 1511389STO-001, Ed. 2 | No | No | No | No | No | No | Yes | 1511389STO-001, Ed. 2 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4150 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1009 | Stiebel Eltron | WPE-I 44 H 400 Premium | WPE-I 44 H 400 Premium | Heating only | Ground Source | 3 | 400 |  |  |  |  | 26.38 | 18.28 | 26.38 | 18.28 | WPE-I 44 H 400 Premium | Heat pump |  | 26.38 | 18.2 | D0000086451-a.pdf | A0857/07.2018 | EN 61000-3-12 | EN 61000-3-11 | Harmonics Flicker Rise 7P06990 2018-01-22 | 7P06990 | No | No | No | No | Yes | No | Yes | 7P06990 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2193 |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
HP_1010 | Stiebel Eltron | WPE-I 12 H Premium | 238612 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 30.65 | 7.05 | 30.65 | 7.05 | WPE-I 12 H Premium | Heat pump | 4017212386125 | 18.05 | 4.152 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1011 | Stiebel Eltron | WPE-I 12 H Premium | 238612 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 43.26 | 9.95 | 43.26 | 9.95 | WPE-I 12 H Premium | Heat pump | 4017212386125 | 18.04 | 4.15 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 13 | 0.05394 | 0.98073 | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1012 | Stiebel Eltron | WPE-I 12 HW 230 GB Premium | 202640 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 30.65 | 7.05 | 30.65 | 7.05 | WPE-I 12 HW 230 GB Premium | Heat pump | 4017212026403 | 18.05 | 4.152 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1013 | Stiebel Eltron | WPE-I 12 HW 230 GB Premium | 202640 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 43.26 | 9.95 | 43.26 | 9.95 | WPE-I 12 HW 230 GB Premium | Heat pump | 4017212026403 | 18.04 | 4.15 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 13 | 0.05394 | 0.98073 | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1014 | Stiebel Eltron | WPE-I 15 H Premium | 238613 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 34.69 | 7.98 | 34.69 | 7.98 | WPE-I 15 H Premium | Heat pump | 4017212386132 | 22.09 | 5.08 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1015 | Stiebel Eltron | WPE-I 15 H Premium | 238613 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 47.31 | 10.88 | 47.31 | 10.88 | WPE-I 15 H Premium | Heat pump | 4017212386132 | 22.09 | 5.08 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 13 | 0.06605 | 0.80092 | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1016 | Stiebel Eltron | WPE-I 15 HW 230 GB Premium | 202621 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 34.69 | 7.98 | 34.69 | 7.98 | WPE-I 15 HW 230 GB Premium | Heat pump | 4017212026410 | 22.09 | 5.08 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.9 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1017 | Stiebel Eltron | WPE-I 15 HW 230 GB Premium | 202621 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 47.31 | 10.88 | 47.31 | 10.88 | WPE-I 15 HW 230 GB Premium | Heat pump | 4017212026410 | 22.09 | 5.08 | D0000094133 | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238613 (WPE-I 15 H 230 Premium 9451-0) Test report for 15kW | 238613 (WPE-I 15 H 230 Premium 9451-0) | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 13 | 0.06605 | 0.80092 | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1018 | Stiebel Eltron | WPE-I 04 H 230 Premium | 202613 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26.9 | 6.187 | 26.9 | 6.187 | WPE-I 04 H 230 Premium | Heat pump | 4017212026137 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1019 | Stiebel Eltron | WPE-I 04 H 230 Premium | 202613 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 39.52 | 9.0896 | 39.52 | 9.0896 | WPE-I 04 H 230 Premium | Heat pump | 4017212026137 | 14.3 | 3.289 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1020 | Stiebel Eltron | WPE-I 04 HW 230 GB Premium | 202637 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26.9 | 6.187 | 26.9 | 6.187 | WPE-I 04 HW 230 GB Premium | Heat pump | 4017212026373 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1021 | Stiebel Eltron | WPE-I 04 HW 230 GB Premium | 202637 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 39.52 | 9.0896 | 39.52 | 9.0896 | WPE-I 04 HW 230 GB Premium | Heat pump | 4017212026373 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1022 | Stiebel Eltron | WPE-I 06 H 230 Premium | 238610 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26.9 | 6.187 | 26.9 | 6.187 | WPE-I 06 H 230 Premium | Heat pump | 4017212386101 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1023 | Stiebel Eltron | WPE-I 06 H 230 Premium | 238610 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 39.52 | 9.0896 | 39.52 | 9.0896 | WPE-I 06 H 230 Premium | Heat pump | 4017212386101 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1024 | Stiebel Eltron | WPE-I 06 HW 230 GB Premium | 202638 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26.9 | 6.187 | 26.9 | 6.187 | WPE-I 06 HW 230 GB Premium | Heat pump | 4017212386101 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1025 | Stiebel Eltron | WPE-I 06 HW 230 GB Premium | 202638 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 39.52 | 9.0896 | 39.52 | 9.0896 | WPE-I 06 HW 230 GB Premium | Heat pump | 4017212386101 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1026 | Stiebel Eltron | WPE-I 08 H 230 Premium | 238611 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26.9 | 6.187 | 26.9 | 6.187 | WPE-I 08 H 230 Premium | Heat pump | 4017212386118 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1027 | Stiebel Eltron | WPE-I 08 H 230 Premium | 238611 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 39.52 | 9.0896 | 39.52 | 9.0896 | WPE-I 08 H 230 Premium | Heat pump | 4017212386118 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1028 | Stiebel Eltron | WPE-I 08 HW 230 GB Premium | 202639 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26.9 | 6.187 | 26.9 | 6.187 | WPE-I 08 HW 230 GB Premium | Heat pump | 4017212026397 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1029 | Stiebel Eltron | WPE-I 08 HW 230 GB Premium | 202639 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 39.52 | 9.0896 | 39.52 | 9.0896 | WPE-I 08 HW 230 GB Premium | Heat pump | 4017212026397 | 14.3 | 3.29 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
[17 empty] | Supplementary (boost) heater - on-board |  | 25.22 | 5.8006 | D0000094133 DoC | D0000094133-A | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 238611 (WPE-I 08 H 230 Premium 9448-0) Test report for the 8kW | 238611 (WPE-I 08 H 230 Premium 9448-0) | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_1030 | Stiebel Eltron | WPL -A 05 HK 230 Premium | 202669 | Heating & Cooling | Air Source | 1 | 230 |  |  | 8.57 |  | 36.08 | 8.298 | 36.08 | 8.298 | WPL -A 05 HK 230 Premium | Heat pump | 4017212026694 | 23.48 | 5.4 | D0000094690 | D0000094690 | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 202829 (WPL-A 05 H 230 Premium 9511-0) | 202829 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 8 | 0.046 | 1.15 | Requires Zsource ≤Zmax | 0.33
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | [17 empty] | N/A | N/A | N/A
HP_1031 | Stiebel Eltron | WPL -A 05 HK 230 Premium | 202669 | Heating & Cooling | Air Source | 1 | 230 |  |  | 8.57 |  | 50.43 | 11.5985 | 50.43 | 11.5985 | WPL -A 05 HK 230 Premium | Heat pump | 4017212026694 | 23.48 | 5.4 | D0000094690 | D0000094690 | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 202829 (WPL-A 05 H 230 Premium 9511-0) | 202829 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 8 | 0.046 | 1.15 | Requires Zsource ≤Zmax | 0.33
[17 empty] | Supplementary (boost) heater - on-board |  | 26.95 | 6.1985 | [17 empty] | N/A | N/A | N/A
HP_1032 | Stiebel Eltron | WPL -A 07 HK 230 Premium | 202669 | Heating & Cooling | Air Source | 1 | 230 |  |  | 12.91 |  | 36.08 | 8.298 | 36.08 | 8.298 | WPL -A 07 HK 230 Premium | Heat pump | 4017212001233 | 23.48 | 5.4 | D0000094690 | D0000094690 | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 202829 (WPL-A 05 H 230 Premium 9511-0) | 202829 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 8 | 0.046 | 1.15 | Requires Zsource ≤Zmax | 0.33
[17 empty] | Supplementary (boost) heater - on-board |  | 12.6 | 2.898 | [17 empty] | N/A | N/A | N/A
HP_1033 | Stiebel Eltron | WPL -A 07 HK 230 Premium | 202669 | Heating & Cooling | Air Source | 1 | 230 |  |  | 12.91 |  | 50.43 | 11.5985 | 50.43 | 11.5985 | WPL -A 07 HK 230 Premium | Heat pump | 4017212001233 | 23.48 | 5.4 | D0000094690 | D0000094690 | EN 61000-3-12 | EN 61000-3-11 | Stiebel Eltron 202829 (WPL-A 05 H 230 Premium 9511-0) | 202829 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 8 | 0.046 | 1.15 | Requires Zsource ≤Zmax | 0.33
[17 empty] | Supplementary (boost) heater - on-board |  | 26.95 | 6.1985 | [17 empty] | N/A | N/A | N/A
HP_1034 | Steibel Eltron | WPL 25 A + 2.6kW heating element | 236644 | Heating only | Air Source | 3 | 400 |  |  |  |  | 12.47 | 8.64 | 20 | 8.64 | 236642 | Whole system |  | 12.47 | 8.56 | WPL (All) - CE - 2019 & EMC_WPL_25_AS | D0000069994-d | EN 61000-3-12 | EN 61000-3-11 | EMV - Stiebel Eltron 236644 (WPL 25 A 9238-0) | Bericht Nummer: 236644 (WPL 25 A 9238-0) | Yes | Yes | Yes | Yes | Yes | Yes | No | EMV - Stiebel Eltron 236644 (WPL 25 A 9238-0) | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_1035 | Steibel Eltron | WPL 25 A + 5.6kW heating element | 236644 | Heating only | Air Source | 3 | 400 |  |  |  |  | 16.81 | 11.65 | 33.05 | 11.65 | 236642 | Whole system |  | 16.81 | 11.56 | WPL (All) - CE - 2019 & EMC_WPL_25_AS | D0000069994-d | EN 61000-3-12 | EN 61000-3-11 | EMV - Stiebel Eltron 236644 (WPL 25 A 9238-0) | Bericht Nummer: 236644 (WPL 25 A 9238-0) | Yes | No | No | No | No | No | Yes | EMV - Stiebel Eltron 236644 (WPL 25 A 9238-0) | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.445
HP_1101 | Vaillant | aroTHERM 5kW | VWL 55/3 A 230V | Heating only | Air Source | 1 | 230 | 8.88 |  |  |  | 15 | 3.45 | 15 | 3.45 | VWL 55/3 A 230V | Heat pump | 0010019758 | 15 | 3.45 | Vaillant_DOC_2017.pdf | Vaillant EN 1601526_01 | EN 61000-3-2 | EN 61000-3-3 |  | FR 654328K/A1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | N/A | N/A | N/A
HP_1102 | Vaillant | aroTHERM 8kW | VWL 85/3 A 230V | Heating only | Air Source | 1 | 230 | 10.4 |  |  |  | 16 | 3.68 | 16 | 3.68 | VWL 85/3 A 230V | Heat pump | 0010019759 | 16 | 3.68 | Vaillant_DOC_2017.pdf | Vaillant EN 1601526_01 | EN 61000-3-2 | EN 61000-3-3 |  | 137614-677048B | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | N/A | N/A | N/A
HP_1103 | Vaillant | flexoTHERM 8kW | VWF 87/4 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 43.1 | 9.91 | 43.1 | 9.91 | VWF 87/4 230V | Heat pump | 0010019759 | 19.1 | 4.39 | DoC flexoTHERM_5_8kW_230v.pdf | Vaillant EN 1601557_01 | EN 61000-3-2 | EN 61000-3-11 | V_VWF_87_4_230V_1EMC_Flicker_INFO_E_VDE_EU_01.pdf | 225373-EC1-1 | Yes | No | No | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.14 | No |  |  | No |  |  | No
[17 empty] | Back-up heater | N/A | 24 | 5.52 | [6 empty] | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.3853
HP_1104 | Vaillant | flexoTHERM 11kW | VWF 117/4 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 48.9 | 11.25 | 48.9 | 11.25 | VWF 117/4 230V | Heat pump | 0010016430 | 24.9 | 4.39 | DoC flexoTHERM_11kW_230v.pdf | Vaillant EN 1601361_01 | EN 61000-3-12 | EN 61000-3-11 | V_VWF_117_4_230V_1EMC_E_VDE_EU_01.pdf | 221760-EC-1-1 | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.15 | No |  |  | No |  |  | No
[17 empty] | Back-up heater | N/A | 24 | 5.52 | [6 empty] | No | No | No | No |  |  | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.3853
HP_1105 | Vaillant | geoTHERM mini | VWS 36/4.1 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 4.7 | 1.08 | 4.7 | 1.08 | VWS 36/4.1 230V | Heat pump |  | 4.7 | 1.08 | Vaillant_geoTHERM_mini_DOC.pdf | Vaillant_geoTHERM_mini_DOC.pdf | EN 61000-3-2 | EN 61000-3-3 | V_VWL_35_4_S_230V_1EMC_E_VDE_EU_01.pdf | 413300-2600-004/161402 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No
HP_1106 | Vaillant | flexoTHERM 5kW | VWF 57/4 230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 35.9 | 8.257 | 35.9 | 8.257 | VWF 57/4 230V | Heat pump | 0010016428 | 11.9 | 2.737 | DoC flexoTHERM_5_8kW_230v.pdf | Vaillant EN 1601557_01 | EN 61000-3-2 | EN 61000-3-11 | V_VWF_57_4_230V_1EMC_E_VDE_EU_01.pdf | 216761-EC1-1 | Yes | No | No | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.42 | No |  |  | No |  |  | No
[17 empty] | Back-up heater | N/A | 24 | 5.52 | [6 empty] | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.39
HP_1107 | Vaillant | aroTHERM split 3.5kW | VWL 35/5 AS 230V S2 + VWL 57/5 IS | Heating only | Air Source | 1 | 230 | 4.91 |  |  |  | 35 | 8.05 | 35 | 8.05 | VWL 35/5 AS 230V S2 | Heat pump | 0010021123 | 11.5 | 2.64 | Vaillant EN 1802336_06_DeclarationOfConformity.pdf | EN 1802336_06 | EN 61000-3-2 | EN 61000-3-3 | V_VWL_35_5_AS_VWL_55_5_AS_1EMC_E_TW_EN_01.pdf | 17-1-0163901T01 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | VWL 57/5 IS | Back-up heater | 0010023498 | 23.5 | 5.4 |  |  | EN 61000-3-2 | EN 61000-3-11 | V_VWL_xx7_5_IS_1EMC_E_TW_EN_01.pdf | P17-Z-00380-002 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.3853
HP_1108 | Vaillant | aroTHERM split 5kW | VWL 55/5 AS 230V S2 + VWL 57/5 IS | Heating only | Air Source | 1 | 230 | 7.87 |  |  |  | 35 | 8.05 | 35 | 8.05 | VWL 55/5 AS 230V S2 | Heat pump | 0010021124 | 11.5 | 2.64 | Vaillant EN 1802336_06_DeclarationOfConformity.pdf | EN 1802336_06 | EN 61000-3-2 | EN 61000-3-3 | V_VWL_35_5_AS_VWL_55_5_AS_1EMC_E_TW_EN_01.pdf | 17-1-0163901T01 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | VWL 57/5 IS | Back-up heater | 0010023498 | 23.5 | 5.4 |  |  | EN 61000-3-2 | EN 61000-3-11 | V_VWL_xx7_5_IS_1EMC_E_TW_EN_01.pdf | P17-Z-00380-002 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.3853
HP_1109 | Vaillant | aroTHERM split 7kW | VWL 75/5 AS 230V S2 + VWL 77/5 IS | Heating only | Air Source | 1 | 230 | 10.78 |  |  |  | 38.4 | 8.83 | 38.4 | 8.83 | VWL 75/5 AS 230V S2 | Heat pump | 0010021125 | 14.9 | 3.42 | Vaillant EN 1802336_06_DeclarationOfConformity.pdf | EN 1802336_06 | EN 61000-3-2 | EN 61000-3-3 | V_VWL_75_5_AS_1EMC_E_TW_EN_01.pdf | 17-1-0163901T01C1 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | VWL 77/5 IS | Back-up heater | 0010023499 | 23.5 | 5.4 |  |  | EN 61000-3-2 | EN 61000-3-11 | V_VWL_xx7_5_IS_1EMC_E_TW_EN_01.pdf | P17-Z-00380-002 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.3853
HP_1110 | Vaillant | aroTHERM split 10kW | VWL 105/5 AS 230V S2 + VWL 127/5 IS | Heating only | Air Source | 1 | 230 | 15.83 |  |  |  | 48.1 | 11.063 | 48.1 | 11.063 | VWL 105/5 AS 230V S2 | Heat pump | 0010024770 | 24.6 | 5.66 | Vaillant EN 1802336_06_DeclarationOfConformity.pdf | EN 1802336_06 | EN 61000-3-12 | EN 61000-3-11 | V_VWL_105_5_AS_230V_VWL_125_5_AS_230V_1EMC_E_TW_EN_01.pdf | 17-1-0206001T02 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.15842 | 0.334 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VWL 127/5 IS | Back-up heater | 0010023524 | 23.5 | 5.4 |  |  | EN 61000-3-12 | EN 61000-3-11 | V_VWL_127_5_IS_1EMC_E_TW_EN_01.pdf | P17-Z-00587-001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.3853
HP_1111 | Vaillant | aroTHERM 11kW | VWL 115/2 A 230V | Heating only | Air Source | 1 | 230 | 13.74 |  |  |  | 20 | 4.6 | 20 | 4.6 | VWL 115/2 A 230V | Heat pump | 0010011972 | 20 | 4.6 | V_VWL 115_2_1EMC_E_HP_00.pdf | 115018-632194Cr2013-06-05 | EN 61000-3-12 | EN 61000-3-11 | V_VWL 115_2_1EMC_E_HP_00.pdf | 115018-632194Cr2013-06-05 | No | Yes | No | No | Yes | No | Yes | Form B aroTHERM 11kW | Equipment complying with IEC 61000-3-12 |  |  | 31 | 0.1426 | 0.371 | Enquipment complying with IEC 61000-3-3 technical requirments |  | No |  |  | No |  |  | No
HP_1112 | Vaillant | aroTHERM 15kW | VWL 155/2 A 230V | Heating only | Air Source | 1 | 230 | 19.73 |  |  |  | 25 | 5.75 | 25 | 5.75 | VWL 155/2 A 230V | Heat Pump | 0010014567 | 25 | 5.75 | aroTHERM 15kW EN61000-3-2 test cert.pdf | FR 654328E/A1 | EN 61000-3-12 | EN 61000-3-11 | V_VWL 155_2_1EMC_E_HP_00.pdf | 126931-654323ACr2014-10-08 | No | No | No | No | Yes | No | Yes | Form B aroTHERM 15kW | Equipment complying with IEC 61000-3-12 |  |  | 29 | 0.1668 | 0.3172 | Requires Service Current Capacity ≥100A per phase |  | No |  |  | No |  |  | No
HP_1113 | Vaillant | aroTHERM split 12kW | VWL 125/5 AS 230V S2 + VWL 127/5 IS | Heating only | Air Source | 1 | 230 | 20.7 |  |  |  | 48.1 | 11.063 | 48.1 | 11.063 | VWL 125/5 AS 230V S2 | Heat pump | 0010021128 | 24.6 | 5.66 | Vaillant EN 1802336_06_DeclarationOfConformity.pdf | EN 1802336_06 | EN 61000-3-12 | EN 61000-3-11 | V_VWL_105_5_AS_230V_VWL_125_5_AS_230V_1EMC_E_TW_EN_01.pdf | 17-1-0206001T02 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1584 | 0.3339 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VWL 127/5 IS | Back-up heater | 0010023524 | 23.5 | 5.4 |  |  | EN 61000-3-12 | EN 61000-3-11 | V_VWL_127_5_IS_1EMC_E_TW_EN_01.pdf | P17-Z-00587-001 | Yes | No | No | No |  |  | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.3853
HP_1114 | Vaillant | flexoTHERM 5kW 400v | VWF 58/4 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 3.6 | 2.49 | 3.6 | 2.49 | VWF 58/4 | Heat pump | 0010016693 | 3.6 | 2.5 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-2 | EN 61000-3-11 | V_VWF_58_4_1EMC_E_VDE_EU_01 | 209632-EC1-3 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1115 | Vaillant | flexoTHERM 8kW 400v | VWF 87/4 400V | Heating only | Ground Source | 3 | 400 |  |  |  |  | 5.48 | 3.8 | 7.36 | 5.1 | VWF 87/4 400V | Heat pump | 0010016694 | 5.48 | 3.8 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-2 | EN 61000-3-11 | V_VWF_87_4_1EMC_Flicker_harmonics_VDE_INFO_E_VDE_EU_01.pdf | 227952-EC1-1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1116 | Vaillant | flexoTHERM 8kW 400v | VWF 87/4 400V | Heating only | Ground Source | 3 | 400 |  |  |  |  | 18.48 | 12.8 | 19 | 13.2 | VWF 87/4 400V | Whole system | 0010016694 | 18.48 | 12.8 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-12 | EN 61000-3-11 | V_VWF_87_4_1EMC_Flicker_harmonics_VDE_INFO_E_VDE_EU_01.pdf | 227952-EC1-1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1117 | Vaillant | flexoTHERM 15kW 400v | VWF 157/4 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 21.8 | 15.1 | 25 | 17.32 | VWF 157/4 | Whole system | 0010016696 | 21.8 | 15.1 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-12 | EN 61000-3-11 | V_VWF_157_4_1EMC_Flicker_harmoics_VDE_INFO_E_VDE_EU_01 | 209632-EC1-1 | Yes | Yes | Yes | Yes | Yes | yes | No | V_VWF_157_4_1EMC_Flicker_harmonics_VDE_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1118 | Vaillant | flexoTHERM 15kW 400v | VWF 157/4 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 8.8 | 6.1 | 9.8 | 6.8 | VWF 157/4 | Heat pump | 0010016696 | 8.8 | 6.1 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-12 | EN 61000-3-11 | V_VWF_157_4_1EMC_Flicker_harmoics_VDE_INFO_E_VDE_EU_01 | 209632-EC1-1 | Yes | Yes | Yes | Yes | Yes | yes | No | V_VWF_157_4_1EMC_Flicker_harmonics_VDE_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1119 | Vaillant | flexoTHERM 19kW 400v | VWF 197/4 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 9.8 | 6.79 | 9.8 | 6.79 | VWF 197/4 | Heat pump | 0010016697 | 9.8 | 6.8 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-12 | EN 61000-3-11 | V-VMF_197_4_1EMC_VDE_E_VDE_EU_01.pdf | 221758-EC1-1 | Yes | Yes | Yes | Yes | Yes | Yes | No | V-VMF_197_4_1EMC_VDE_E_VDE_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1120 | Vaillant | flexoTHERM 11kW 400v | VWF 117/4 400v | Heating only | Ground Source | 3 | 400 |  |  |  |  | 5.34 | 3.7 | 5.34 | 3.7 | VWF 117/4 400v | Heat pump | 0010016695 | 5.34 | 3.7 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-12 | EN 61000-3-11 | V-VMF_117_4_1EMC_Flicker_harmonics_VDE_INFO_E_VDE_EU_01.pdf | 227952-EC1-2 | No | Yes | No | No | Yes | No | Yes | V_VWF_117_4_1EMC_Flicker_harmoics_VDE_INFO_E_VDE_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1121 | Vaillant | flexoTHERM 11kW 400v | VWF 117/4 400v | Heating only | Ground Source | 3 | 400 |  |  |  |  | 18.34 | 12.71 | 19 | 12.71 | VWF 117/4 400v | Whole system | 0010016695 | 18.34 | 12.71 | DoC flexoTHERM 400v | Vaillant 0622015 | EN 61000-3-12 | EN 61000-3-11 | V-VMF_117_4_1EMC_Flicker_harmonics_VDE_INFO_E_VDE_EU_01.pdf | 227952-EC1-2 | No | Yes | No | No | Yes | No | Yes | V_VWF_117_4_1EMC_Flicker_harmoics_VDE_INFO_E_VDE_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.3949 | 0.405 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1122 | Vaillant | aroTHERM plus 5kW & AI | VWL 55/6 A 230V S2 | Heating only | Air Source | 1 | 230 | 10 |  |  |  | 14.3 | 3.29 | 14.3 | 3.29 | VWL 55/6 A 230V S2 | Heat pump | 0010021131 & 0010031644 | 14.3 | 3.4 | DoC aroTHERM_plus_Declaration_of_conformity.pdf | Vaillant EN 1902738_01 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_5kw_test_repot_19-1-0032401T01-C1.pdf | 19-1-0032401T01-C1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1123 | Vaillant | aroTHERM plus 5kW + hydraulic module | VWL 55/6 A 230V S2 & VWZ MEH 97/5 MB2 | Heating only | Air Source | 1 | 230 | 10 |  |  |  | 39.3 | 9.04 | 39.3 | 9.04 | VWL 55/6 A 230V S2 | Heat pump | 0010021131 | 14.3 | 3.4 | DoC aroTHERM_plus_Declaration_of_conformity.pdf | Vaillant EN 1902738_01 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_5kw_test_repot_19-1-0032401T01-C1.pdf | 19-1-0032401T01-C1 | Yes | Yes | Yes | Yes | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VWZ MEH 97/5 MB2 | Back-up heater - external | 0010023610 | 25 | 5.41 | DoC_Hydraulic module_Vaillant EN 1902741_02.pdf | Vaillant EN 1902741_02 | EN 61000-3-12 | EN 61000-3-11 | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-002 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1124 | Vaillant | aroTHERM plus 7kW & AI | VWL 75/6 A 230V S2 | Heating only | Air Source | 1 | 230 | 11.5 |  |  |  | 15 | 3.45 | 15 | 3.45 | VWL 75/6 A 230V S2 | Heat pump | 0010021132 & 0010031644 | 15 | 3.5 | DoC aroTHERM_plus_Declaration_of_conformity | Vaillant EN 1902738_01 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_7kw_test_repot_19-1-0032501T01-C1.pdf | 19-1-0032501T01-C1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1125 | Vaillant | aroTHERM plus 7kW + hydraulic module | VWL 75/6 A 230V S2 & VWZ MEH 97/5 MB2 | Heating only | Air Source | 1 | 230 | 11.5 |  |  |  | 40 | 9.2 | 40 | 9.2 | VWL 75/6 A 230V S2 | Heat pump | 0010021132 | 15 | 3.5 | DoC aroTHERM_plus_Declaration_of_conformity | Vaillant EN 1902738_01 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_7kw_test_repot_19-1-0032501T01-C1 | 19-1-0032501T01-C1 | Yes | Yes | Yes | Yes | No | No | Yes | aroTHERM_plus_7kw_test_repot_19-1-0032501T01-C1.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VWZ MEH 97/5 MB2 | Back-up heater - external | 0010023610 | 25 | 5.41 | DoC_Hydraulic module_Vaillant EN 1902741_02 | Vaillant EN 1902741_02 | EN 61000-3-12 | EN 61000-3-11 | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-002 | Yes | Yes | Yes | Yes |  | No | Yes | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1126 | Vaillant | aroTHERM plus 3.5kW + hydraulic module | VWL 35/6 A 230V S2 & VWZ MEH 97/5 MB2 | Heating only | Air Source | 1 | 230 | 6.1 |  |  |  | 39.3 | 9.04 | 39.3 | 9.04 | VWL 35/6 A 230V S2 | Heat pump | 0010021130 | 14.3 | 3.4 | Doc aroTHERM plus Vaillant EN 1902738_04.pdf | Vaillant EN 1902738_04 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_5kw_test_repot_19-1-0032401T01-C1.pdf | 19-1-0032401T01-C1 | Yes | Yes | Yes | Yes | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VWZ MEH 97/5 MB2 | Back-up heater - external | 0010023610 | 25 | 5.41 | DoC_Hydraulic module_Vaillant EN 1902741_02.pdf | Vaillant EN 1902741_02 | EN 61000-3-12 | EN 61000-3-11 | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-002 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1127 | Vaillant | aroTHERM plus 3.5kW & AI | VWL 35/6 A 230V S2 | Heating only | Air Source | 1 | 230 | 6.1 |  |  |  | 14.3 | 3.29 | 14.3 | 3.29 | VWL 35/6 A 230V S2 | Heat pump | 0010021130 & 0010031644 | 14.3 | 3.4 | Doc aroTHERM plus Vaillant EN 1902738_04.pdf | Vaillant EN 1902738_04 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_5kw_test_repot_19-1-0032401T01-C1.pdf | 19-1-0032401T01-C1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1128 | Vaillant | aroTHERM plus 3.5kW + uniTOWER | VWL 35/6 A 230V S2 & VIH QW 190/6 E GB MB8 | Heating only | Air Source | 1 | 230 | 6.1 |  |  |  | 37.8 | 8.69 | 37.8 | 8.69 | VWL 35/6 A 230V S2 | Heat pump | 0010021130 | 14.3 | 3.4 | Doc aroTHERM plus Vaillant EN 1902738_04.pdf | Vaillant EN 1902738_04 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_5kw_test_repot_19-1-0032401T01-C1.pdf | 19-1-0032401T01-C1 | Yes | Yes | Yes | Yes | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | VIH QW 190/6 E GB MB8 | Back-up heater - external | 0010022093 | 23.5 | 5.4 | DOC_uniTOWER_Vaillant DE 1902747_01.pdf | Vaillant DE 1902747_01 | EN 61000-3-12 | EN 61000-3-11 | V_VIH_QW_190_6_E_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-001 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1129 | Vaillant | aroTHERM plus 5kW + uniTOWER | VWL 55/6 A 230V S2 & VIH QW 190/6 E GB MB8 | Heating only | Air Source | 1 | 230 | 10 |  |  |  | 37.8 | 8.69 | 37.8 | 8.69 | VWL 55/6 A 230V S2 | Heat pump | 0010021131 | 14.3 | 3.4 | DoC aroTHERM_plus_Declaration_of_conformity.pdf | Vaillant EN 1902738_01 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_5kw_test_repot_19-1-0032401T01-C1.pdf | 19-1-0032401T01-C1 | Yes | Yes | Yes | Yes | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | VIH QW 190/6 E GB MB8 | Back-up heater - external | 0010022093 | 23.5 | 5.4 | DOC_uniTOWER_Vaillant DE 1902747_01.pdf | Vaillant DE 1902747_01 | EN 61000-3-12 | EN 61000-3-11 | V_VIH_QW_190_6_E_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-001 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1130 | Vaillant | aroTHERM plus 7kW + uniTOWER | VWL 75/6 A 230V S2 & VIH QW 190/6 E GB MB8 | Heating only | Air Source | 1 | 230 | 11.5 |  |  |  | 38.5 | 8.86 | 38.5 | 8.86 | VWL 75/6 A 230V S2 | Heat pump | 0010021132 | 15 | 3.5 | DoC aroTHERM_plus_Declaration_of_conformity.pdf | Vaillant EN 1902738_01 | EN 61000-3-2 | EN 61000-3-3 | aroTHERM_plus_7kw_test_repot_19-1-0032501T01-C1.pdf | 19-1-0032501T01-C1 | Yes | Yes | Yes | Yes | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | VIH QW 190/6 E GB MB8 | Back-up heater - external | 0010022093 | 23.5 | 5.4 | DOC_uniTOWER_Vaillant DE 1902747_01.pdf | Vaillant DE 1902747_01 | EN 61000-3-12 | EN 61000-3-11 | V_VIH_QW_190_6_E_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-001 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1131 | Vaillant | aroTHERM plus 10kW & AI | VWL 105/6 A 230V S2 | Heating only | Air Source | 1 | 230 | 15.4 |  |  |  | 23.3 | 5.36 | 23.3 | 5.36 | VWL 105/6 A 230V S2 | Heat pump | 0010021133 & 0010031644 | 23.3 | 5.4 | aroTHERM plus_12kW DoC Vaillant DE 1902740_04.pdf | Vaillant DE 1902740_04 | EN 61000-3-12 | EN 61000-3-11 | aroTHERM_plus_10_12kw_test_report_19-1-0032601T01-C3.pdf | 19-1-0032601T01-C3 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1132 | Vaillant | aroTHERM plus 10kW + hydraulic module | VWL 105/6 A 230V S2 & VWZ MEH 97/5 MB2 | Heating only | Air Source | 1 | 230 | 15.4 |  |  |  | 48.3 | 11.11 | 48.3 | 11.11 | VWL 105/6 A 230V S2 | Heat pump | 0010021133 | 23.3 | 5.4 | aroTHERM plus 10_12kW DoC Vaillant DE 1902740_04.pdf | Vaillant DE 1902740_04 | EN 61000-3-12 | EN 61000-3-11 | aroTHERM_plus_10_12kw_test_report_19-1-0032601T01-C3.pdf | 19-1-0032601T01-C3 | No | Yes | No | No | No | No | Yes | aroTHERM_plus_10_12kw_test_report_19-1-0032601T01-C3.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VWZ MEH 97/5 MB2 | Back-up heater - external | 0010023610 | 25 | 5.75 | DoC_Hydraulic module_Vaillant EN 1902741_02 | Vaillant EN 1902741_02 | EN 61000-3-12 | EN 61000-3-11 | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-002 | Yes | Yes | Yes | Yes |  | No | Yes | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1133 | Vaillant | aroTHERM plus 10kW + uniTOWER | VWL 105/6 A 230V S2 & VIH QW 190/6 E GB MB8 | Heating only | Air Source | 1 | 230 | 15.4 |  |  |  | 46.8 | 10.76 | 46.8 | 10.76 | VWL 105/6 A 230V S2 | Heat pump | 0010021133 | 23.3 | 5.4 | aroTHERM plus 10_12kW DoC Vaillant DE 1902740_04.pdf | Vaillant DE 1902740_04 | EN 61000-3-12 | EN 61000-3-11 | aroTHERM_plus_10_12kw_test_report_19-1-0032601T01-C3.pdf | 19-1-0032601T01-C3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VIH QW 190/6 E GB MB8 | Back-up heater - external | 0010022093 | 23.5 | 5.41 | DOC_uniTOWER_Vaillant DE 1902747_01.pdf | Vaillant DE 1902747_01 | EN 61000-3-12 | EN 61000-3-11 | V_VIH_QW_190_6_E_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-001 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1134 | Vaillant | aroTHERM plus 12kW & AI | VWL 125/6 A 230V S2 | Heating only | Air Source | 1 | 230 | 20.1 |  |  |  | 23.3 | 5.36 | 23.3 | 5.36 | VWL 125/6 A 230V S2 | Heat pump | 0010021135 & 0010031644 | 23.3 | 5.4 | aroTHERM plus 10_12kW DoC Vaillant DE 1902740_04.pdf | Vaillant DE 1902740_04 | EN 61000-3-12 | EN 61000-3-11 | aroTHERM_plus_10_12kw_test_report_19-1-0032601T01-C3.pdf | 19-1-0032601T01-C3 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.1608 | 0.32904 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1135 | Vaillant | aroTHERM plus 12kW + hydraulic module | VWL 125/6 A 230V S2 & VWZ MEH 97/5 MB2 | Heating only | Air Source | 1 | 230 | 20.1 |  |  |  | 48.3 | 11.11 | 48.3 | 11.11 | VWL 125/6 A 230V S2 | Heat pump | 0010021135 | 23.3 | 5.4 | aroTHERM plus 10_12kW DoC Vaillant DE 1902740_04.pdf | Vaillant DE 1902740_04 | EN 61000-3-12 | EN 61000-3-11 | aroTHERM_plus_10_12kw_test_report_19-1-0032601T01-C3.pdf | 19-1-0032601T01-C3 | No | Yes | No | No | No | No | Yes | aroTHERM_plus_12kw_test_report_19-1-0032601T01-C3.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VWZ MEH 97/5 MB2 | Back-up heater - external | 0010023610 | 25 | 5.41 | DoC_Hydraulic module_Vaillant EN 1902741_02 | Vaillant EN 1902741_02 | EN 61000-3-12 | EN 61000-3-11 | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-002 | Yes | Yes | Yes | Yes |  | No | Yes | V_VWZ_MEH_97_6_1EMC_E_EMC_Test_NRW_EU_01.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1136 | Vaillant | aroTHERM plus 12kW + uniTOWER | VWL 125/6 A 230V S2 & VIH QW 190/6 E GB MB8 | Heating only | Air Source | 1 | 230 | 20.1 |  |  |  | 46.8 | 10.76 | 46.8 | 10.76 | VWL 125/6 A 230V S2 | Heat pump | 0010021135 | 23.3 | 5.4 | aroTHERM plus 10_12kW DoC Vaillant DE 1902740_04.pdf | Vaillant DE 1902740_04 | EN 61000-3-12 | EN 61000-3-11 | aroTHERM_plus_10_12kw_test_report_19-1-0032601T01-C3.pdf | 19-1-0032601T01-C3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.1608 | 0.32904 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | VIH QW 190/6 E GB MB8 | Back-up heater - external | 0010022093 | 23.5 | 5.41 | DOC_uniTOWER_Vaillant DE 1902747_01.pdf | Vaillant DE 1902747_01 | EN 61000-3-12 | EN 61000-3-11 | V_VIH_QW_190_6_E_1EMC_E_EMC_Test_NRW_EU_01.pdf | P19-Z-00017-001 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1201 | Warmflow | GS08 | GS08 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 30 | 6.9 | 30 | 6.9 | GS08 | Heat pump |  | 30 | 6.9 | WDC032 Ground Source Heat Pumps.pdf | WDC032 |  |  |  |  | Yes | No | No | No | Yes | No | Yes | Warmflow GS08 Current Harmonic Summary rev2.xlsx | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.254 | No |  |  | No |  |  | No
HP_1202 | Warmflow | GS16 | GS16 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 40 | 9.2 | 40 | 9.2 | GS16 | Heat pump |  | 40 | 9.2 | WDC032 Ground Source Heat Pumps.pdf | WDC032 |  |  |  |  | Yes | No | No | No | No | No | Yes | Warmflow GS16 Current Harmonic Summary rev2.xlsx | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.191 | No |  |  | No |  |  | No
HP_1203 | Warmflow | Zeno | AS02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | AS02 | Heat pump |  | 18 | 4.14 | WDC036 ASHP EC Declaration of Conformity | WDC036 | EN 61000-3-12 | EN 61000-3-11 | GZEM151200647201.pdf | GZEM151200647201 | Yes | Yes | Yes | Yes | Yes | Yes | No | GZEM151200647201.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_1204 | Warmflow | Zeno | AS01 | Heating only | Air Source | 1 | 230 |  |  |  |  | 9 | 2.07 | 9 | 2.07 | AS01 | Heat pump |  | 9 | 2.07 | WDC036 ASHP EC Declaration of Conformity | WDC036 | EN 61000-3-2 | EN 61000-3-3 | GZEM151200647201.pdf | GZEM151200647201 | Yes | Yes | Yes | Yes | Yes | Yes | No | GZEM151200647201.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1205 | Warmflow | Zeno | AS01-R32 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | AS01-R32 | Whole system |  | 13 | 2.99 | 64711200290901 CERT_EMC(P6,P10A.P17A).pdf | E8A 082795 0067 | EN 61000-3-2 | EN 61000-3-3 | 64711200290901TRF_EMC(P6P10A.P17A).pdf | 64.711.20.02909.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 64.711.20.02909.01 | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1206 | Warmflow | Zeno | AS02-R32 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 21.5 | 4.95 | 21.5 | 4.95 | AS02-R32 | Whole system |  | 21.5 | 4.95 | 64711200290901 CERT_EMC(P6,P10A.P17A).pdf | E8A 082795 0067 | EN 61000-3-12 | EN 61000-3-11 | 64711200290901TRF_EMC(P6P10A.P17A).pdf | 64.711.20.02909.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 64.711.20.02909.01 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1207 | Warmflow | Zeno | AS03-R32 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 33.2 | 7.636 | 33.2 | 7.64 | AS03-R32 | Whole system |  | 33.2 | 7.64 | 64711200290901 CERT_EMC(P6,P10A.P17A).pdf | E8A 082795 0067 | EN 61000-3-12 | EN 61000-3-11 | 64711200290901TRF_EMC(P6P10A.P17A).pdf | 64.711.20.02909.01 | No | Yes | No | No | No | No | Yes | 64.711.20.02909.01 | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.2138 | 0.2474 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1208 | Warmflow | Zeno | AS03 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27 | 6.21 | 27 | 6.21 | AS03 | Whole system |  | 27 | 6.21 | WDC036 ASHP EC Declaration of Conformity.pdf | WDC036 | EN 61000-3-12 | EN 61000-3-11 | H15B 64.711.20.02828.01 EMC Test Report.pdf | 64.711.20.02828.01 | No | Yes | No | No | Yes | No | Yes | 64.711.20.02909.01 | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.0787 | 0.6725 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1209 | Warmflow | Zeno | AS02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | AS02 | Heat pump |  | 18 | 4.14 | WDC036 ASHP EC Declaration of Conformity | WDC036 | EN 61000-3-12 | EN 61000-3-11 | GZEM151200647201.pdf | GZEM151200647201 | Yes | Yes | Yes | Yes | Yes | Yes | No | GZEM151200647201.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1210 | Warmflow | Zeno | AS01 | Heating only | Air Source | 1 | 230 |  |  |  |  | 9 | 2.07 | 9 | 2.07 | AS01 | Heat pump |  | 9 | 2.07 | WDC036 ASHP EC Declaration of Conformity | WDC036 | EN 61000-3-2 | EN 61000-3-3 | GZEM151200647201.pdf | GZEM151200647201 | Yes | Yes | Yes | Yes | Yes | Yes | No | GZEM151200647201.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1211 | Warmflow | Zeno | AS01-R32 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | AS01-R32 | Whole system |  | 13 | 2.99 | 64711200290901 CERT_EMC(P6,P10A.P17A).pdf | E8A 082795 0067 | EN 61000-3-2 | EN 61000-3-3 | 64711200290901TRF_EMC(P6P10A.P17A).pdf | 64.711.20.02909.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 64.711.20.02909.01 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1212 | Warmflow | Zeno | AS02-R32 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 21.5 | 4.95 | 21.5 | 4.95 | AS02-R32 | Whole system |  | 21.5 | 4.95 | 64711200290901 CERT_EMC(P6,P10A.P17A).pdf | E8A 082795 0067 | EN 61000-3-12 | EN 61000-3-11 | 64711200290901TRF_EMC(P6P10A.P17A).pdf | 64.711.20.02909.01 | Yes | Yes | Yes | No | Yes | No | Yes | 64.711.20.02909.01 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 26 | 5.98 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.246
HP_1213 | Warmflow | Zeno | AS03-R32 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 33.2 | 7.636 | 33.2 | 7.64 | AS03-R32 | Whole system |  | 33.2 | 7.64 | 64711200290901 CERT_EMC(P6,P10A.P17A).pdf | E8A 082795 0067 | EN 61000-3-12 | EN 61000-3-11 | 64711200290901TRF_EMC(P6P10A.P17A).pdf | 64.711.20.02909.01 | No | Yes | No | No | No | No | Yes | 64.711.20.02909.01 | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.2138 | 0.2474 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 39 | 8.97 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.164
HP_1214 | Warmflow | Zeno | AS03 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27 | 6.21 | 27 | 6.21 | AS03 | Whole system |  | 27 | 6.21 | WDC036 ASHP EC Declaration of Conformity.pdf | WDC036 | EN 61000-3-12 | EN 61000-3-11 | H15B 64.711.20.02828.01 EMC Test Report.pdf | 64.711.20.02828.01 | No | Yes | No | No | Yes | No | Yes | 64.711.20.02909.01 | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.0787 | 0.6725 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 39 | 8.97 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.164
HP_1301 | Ecoforest | ecoGEO T 5-22 kW | ecoGEO T 5-22 kW | Heating only | Ground Source | 3 | 400 |  |  |  |  | 11.1 | 7.6903 | 11.1 | 7.6903 | ecoGEO 5-22 kW | Whole system | EBFH00 | 11.1 | 7.7 | ECOFOREST CE MARKING.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 2419/0167-F.pdf | 2419/0167-F | No | Yes | No | No | Yes | No | Yes | EMC test report 2419-0167-F.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1081 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1302 | Ecoforest | ecoGEO T 1-9 kW | ecoGEO T 1-9 kW | Heating only | Ground Source | 3 | 400 |  |  |  |  | 5.5 | 3.8105 | 5.5 | 3.8105 | ecoGEO 1-9 kW | Whole system | EBDB00 | 5.5 | 4 | ECOFOREST CE MARKING.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 2419/0167-F.pdf | 2419/0167-F | No | Yes | No | No | Yes | No | Yes | EMC test report 2419-0167-F.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1081 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1303 | Ecoforest | ecoGEO T 3-12 kW | ecoGEO T 3-12 kW | Heating only | Ground Source | 3 | 400 |  |  |  |  | 7.2 | 4.9883 | 7.2 | 4.9883 | ecoGEO 3-12 kW | Whole system | EBFC00 | 7.2 | 6 | ECOFOREST CE MARKING.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 2419/0167-F.pdf | 2419/0167-F | No | Yes | No | No | Yes | No | Yes | EMC test report 2419-0167-F.pdf | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1081 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1304 | Ecoforest | ecoGEO 5-22 kW | ecoGEO 5-22 kW | Heating only | Ground Source | 1 | 230 |  |  |  |  | 23.9 | 5.497 | 23.9 | 5.497 | ecoGEO 5-22 kW | Whole system | EBED00 | 23.9 | 5.8 | ECOFOREST CE MARKING.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 2419/0167-F.pdf | 2419/0167-F | No | No | No | No | Yes | No | Yes | EMC test report 2419-0167-F.pdf | Equipment complying with IEC 61000-3-12 |  |  | 16 | 0.07728 | 0.68452 | Requires Zsource ≤Zmax | 0.36 | No |  |  | No |  |  | No
HP_1305 | Ecoforest | ecoGEO 1-9 kW | ecoGEO 1-9 kW | Heating only | Ground Source | 1 | 230 |  |  |  |  | 17.4 | 4 | 17.4 | 4 | ecoGEO 1-9 kW | Whole system | EBCB00 | 17.4 | 4 | ECOFOREST CE MARKING.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 2419/0167-F.pdf | 2419/0167-F | No | No | No | No | Yes | No | Yes | EMC test report 2419-0167-F.pdf | Equipment complying with IEC 61000-3-12 |  |  | 16 | 0.07728 | 0.68452 | Requires Zsource ≤Zmax | 0.36 | No |  |  | No |  |  | No
HP_1306 | Ecoforest | ecoGEO 3-12 kW | ecoGEO 3-12 kW | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26.5 | 6.1 | 26.5 | 6.1 | ecoGEO 3-12 kW | Whole system | EBEC00 | 26.5 | 6.1 | ECOFOREST CE MARKING.pdf |  | EN 61000-3-12 | EN 61000-3-11 | EMC test report 2419/0167-F.pdf | 2419/0167-F | No | No | No | No | Yes | No | Yes | EMC test report 2419-0167-F.pdf | Equipment complying with IEC 61000-3-12 |  |  | 16 | 0.07728 | 0.68452 | Requires Zsource ≤Zmax | 0.36 | No |  |  | No |  |  | No
HP_1307 | Ecoforest | ecoGEO 12-40 kW | ecoGEO 12-40 kW | Heating only | Ground Source | 3 | 400 |  |  |  |  | 24.6 | 17.0434 | 24.6 | 17.0434 | ecoGEO 12-40 kW | Whole system | EATKA0 | 24.6 | 17.0434 | ECOFOREST CE MARKING.pdf | EC DECLARATION OF CONFORMITY | EN 61000-3-12 | EN 61000-3-11 | 2219-0301_ECOFOREST-ECOGEO HP3 25-100 | 2219/0301 | No | No | No | No | Yes | No | Yes | 2219-0301_ECOFOREST-ECOGEO HP3 25-100 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4206 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.17 | No |  |  | No |  |  | No
HP_1308 | Ecoforest | ecoGEO 15-70 kW | ecoGEO 15-70 kW | Heating only | Ground Source | 3 | 400 |  |  |  |  | 32.3 | 22.3781 | 32.3 | 22.3781 | ecoGEO 15-70 kW | Whole system | EATLA0 | 32.3 | 20.4 | ECOFOREST CE MARKING.pdf | EC DECLARATION OF CONFORMITY | EN 61000-3-12 | EN 61000-3-11 | 2219-0301_ECOFOREST-ECOGEO HP3 25-100 | 2219/0301 | No | No | No | No | No | No | Yes | 2219-0301_ECOFOREST-ECOGEO HP3 25-100 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4206 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.17 | No |  |  | No |  |  | No
HP_1309 | Ecoforest | ecoGEO 25-100 kW | ecoGEO 25-100 kW | Heating only | Ground Source | 3 | 400 |  |  |  |  | 45.1 | 31.2462 | 45.1 | 31.2462 | ecoGEO 25-100 kW | Whole system | EATMA0 | 45.1 | 29.1 | ECOFOREST CE MARKING.PDF | EC DECLARATION OF CONFORMITY | EN 61000-3-12 | EN 61000-3-11 | 2219-0301_ECOFOREST-ECOGEO HP3 25-100 | 2219/0301 | No | No | No | No | No | No | Yes | 2219-0301_ECOFOREST-ECOGEO HP3 25-100 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4206 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.17 | No |  |  | No |  |  | No
HP_1310 | Ecoforest | ecoAIR T EVI 4-20 | ecoAIR T EVI 4-20 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13 | 9.0067 | 13 | 9.0067 | ecoAIR T EVI 4-20 | Heat pump | EQLFA0 | 13 | 9 | 2021_01_11_EC Declaration of Conformity_ecoAIR | Ecoforest Geotermia SL CE20191112 | EN 61000-3-2 | EN 61000-3-3 | 2220-0265_3_ECOFOREST-ECOAIR_EVI T 4-20_ EVI 4-20.pdf | 2220/0265/3 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1311 | Ecoforest | ecoAIR T 3-12 PRO | ecoAIR T 3-12 PRO | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 12 | 8.31 | 12 | 8.31 | ecoAIR T 3-12 PRO | Heat pump | EPNGA0 | 12 | 8.31 | 2021_01_11_EC Declaration of Conformity_ecoAIR | Ecoforest Geotermia SL CE20191112 | EN 61000-3-2 | EN 61000-3-3 | 2220-0265_1_ECOFOREST-ECOAIR_T 3-12 PRO.pdf | 2220/0265/1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1312 | Ecoforest | ecoAIR EVI 4-20 | ecoAIR EVI 4-20 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 36 | 8.28 | 36 | 8.28 | ecoAIR EVI 4-20 | Heat pump | EQKFA0 | 36 | 8.28 | 2021_01_11_EC Declaration of Conformity_ecoAIR.pdf | Ecoforest Geotermia SL CE 20191112 | EN 61000-3-12 | EN 61000-3-11 | 2220-0265_3_ECOFOREST-ECOAIR_EVI T 4-20_ EVI 4-20.pdf | 2220/0265/3 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.15732 | 0.33626 | Requires Zsource ≤Zmax | 0.17 | No |  |  | No |  |  | No
HP_1313 | Ecoforest | ecoAIR 3-12 PRO | ecoAIR 3-12 PRO | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | 5.06 | Heat pump | EPSGA0 | 22 | 5.06 | 2021_01_11_EC Declaration of Conformity_ecoAIR | Ecoforest Geotermia SL CE20191112 | EN 61000-3-12 | EN 61000-3-11 | 2220-0265_1_ECOFOREST-ECOAIR_T 3-12 PRO.pdf | 2220/0265/1 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1224 | 0.43233 | Requires Zsource ≤Zmax | 0.35 | No |  |  | No |  |  | No
HP_1314 | Ecoforest | ecoAIR 1-7 PRO | ecoAIR 1-7 PRO | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | ecoAIR 1-7 PRO | Heat pump | ERRJA0 | 13 | 2.99 | 2021_01_11_EC Declaration of Conformity_ecoAIR | Ecoforest Geotermia SL CE20191112 | EN 61000-3-2 | EN 61000-3-3 | 2220-0265_2A_ECOFOREST-ECOAIR_1-7 PRO | 2220/0265/2A | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1315 | Ecoforest | ecoGEO 1-6 kW PRO | ecoGEO C4 1-6kW PRO | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | ecoGEO C4 1-6kW PRO | Heat pump |  | 13 | 2.99 | 2020_01_09_EC Declaration of Conformity_ecoGEO.pdf | Ecoforest Geotermia SL CE20191112 | EN 61000-3-2 | EN 61000-3-3 | 2221-0337-1_ECOFOREST-ECOGEO C4 1-6 kW PRO.pdf | 2221/0337/1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1316 | Ecoforest | ecoAIR 3-18 PRO | EQUOA0 | Heating only | Air Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | EQUOA0 | Heat pump |  | 26 | 5.98 | 2021_11_01_EC Declaration of ConformityECOFOREST.pdf | CE 20191112 | EN 61000-3-12 | EN 61000-3-11 | 2221-0368_ECOFOREST-ECOAIR_3-18 PRO.pdf | 221-0368 | No | No | No | No | Yes | No | Yes | 2221-0368_ECOFOREST-ECOAIR_3-18 PRO.pdf | Equipment complying with IEC 61000-3-12 |  |  | 21 | 0.03684 | 1.369 | Requires Zsource ≤Zmax | 0.27
HP_1317 | Ecoforest | ecoAIR T 3-18 PRO | EQSOA0 | Heating only | Air Source | 3 | 400 |  |  |  |  | 12 | 8.313 | 12 | 8.313 | EQSOA0 | Heat pump |  | 12 | 8.313 | 2021_12_23_EC Declaration of ConformityECOFOREST.pdf | CE 20191112 | EN 61000-3-2 | EN 61000-3-3 | 2221-0368_ECOFOREST-ECOAIR_3-18 PRO.pdf | 221-0368 | Yes | Yes | Yes | Yes | Yes | Yes | No | 2221-0368_ECOFOREST-ECOAIR_3-18 PRO.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1401 | Grant | Aerona3 | HPID6R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 11.2 | 2.58 | 11.2 | 2.58 | HPID6R32 | Heat pump |  | 11.2 | 2.57 | GUK041906 CE DoC HPID6R32 | GUK041906 CE DoC HPID6R32 | EN 61000-3-2 | EN 61000-3-3 | CH-EMC-18015 EMC TEST REPORT | CH-EMC-18015 | Yes | Yes | Yes | Yes | Yes | Yes | No | Form A HPID6R32.pdf | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No |  | Yes | No |  | No
HP_1402 | Grant | Aerona3 | HPID10R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 17.5 | 4.03 | 17.5 | 4.03 | HPID10R32 | Heat pump |  | 17.5 | 4.02 | GUK041910 CE DoC HPID10R32 | GUK041910 CE DoC HPID10R32 | EN 61000-3-12 | EN 61000-3-11 | AEYC-1047XU-GR EMC TEST REPORT | CH-EMC-22001 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | No
HP_1403 | Grant | Aerona3 | HPID13R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | HPID13R32 | Heat Pump |  | 22 | 5.06 | GUK041913 CE DoC HPID13R32 | GUK041913 CE DoC HPID13R32 | EN 61000-3-12 | EN 61000-3-11 | 20230116 HPID13R32 (AEYC-1248XU-GR)_EMC TEST REPORT | CH-EMC-22002 | Yes | Yes | Yes | Yes | Yes | Yes | No | Form B HPID13R32.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | No
HP_1404 | Grant | Aerona3 | HPID17R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 25.3 | 5.82 | 25.3 | 5.82 | HPID17R32 | Heat pump |  | 25.3 | 5.82 | GUK041917 CE DoC HPID17R32 | GUK041917 CE DoC HPID17R32 | EN 61000-3-12 | EN 61000-3-11 | AEYC-1643XU-CH(BA) EMC TEST REPORT | CH-EMC-18012 | No | No | No | No | Yes | No | Yes | Form B HPID17R32.pdf | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.0989 | 0.535 | Requires Zsource ≤Zmax | 0.306 | Yes | No |  | Yes | No |  | No
HP_1501 | Hitachi | Yutaki S 2 HP 410A | RAS-2WHVNP / RWM-2.0NE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25.5 | 5.87 | 25.5 | 5.87 | RAS-2WHVNP / RWM-2.0NE | Heat pump |  | 12.4 | 2.85 | 17F20445xA_r0_RAS-WHNP | 17F20445xA | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.2 | 0.05 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1502 | Hitachi | Yutaki S 2.5 HP 410A | RAS-2.5WHVNP / RWM-2.5NE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.3 | 6.28 | 27.3 | 6.28 | RAS-2.5WHVNP / RWM-2.5NE | Heat pump |  | 14.2 | 3.27 | 17F20445xA_r0_RAS-WHNP | 17F20445xA | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.2 | 0.05 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1503 | Hitachi | Yutaki S 3.0 HP 410A | RAS-3WHVNP / RWM-3.0NE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 29.1 | 6.69 | 29.1 | 6.69 | RAS-3WHVNP / RWM-3.0NE | Heat pump |  | 16 | 3.68 | 17F20445xA_r0_RAS-WHNP | 17F20445xA | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.2 | 0.05 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1504 | Hitachi | Yutaki S 4.0 HP 410A | RAS-4WHVNPE / RWM-4.0NE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.5 | 12.31 | 53.5 | 12.31 | RAS-4WHVNPE / RWM-4.0NE | Heat pump |  | 27.4 | 6.3 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25 | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.3 | 0.07 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-12 | EN 61000-3-11 |  |  | No | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 25.8 | 5.93 | [9 empty] | No |  | No | Yes |  |  |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
HP_1505 | Hitachi | Yutaki S 4.0 HP 3Ph | RAS-4WHNPE / RWM-4.0NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21.5 | 14.9 | 21.5 | 14.9 | RAS-4WHNPE / RWM-4.0NE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.3 | 0.21 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 8.6 | 5.96 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1506 | Hitachi | Yutaki S 5.0 HP 410A | RAS-5WHVNPE / RWM-5.0NE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.5 | 12.31 | 53.5 | 12.31 | RAS-5WHVNPE / RWM-5.0NE | Heat pump |  | 27.4 | 6.3 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25 | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.3 | 0.07 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-12 | EN 61000-3-11 |  |  | No | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 25.8 | 5.93 | [9 empty] | No |  | No | Yes |  |  |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
HP_1507 | Hitachi | Yutaki S 5.0 HP 3Ph | RAS-5WHNPE / RWM-5.0NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21.5 | 14.9 | 21.5 | 14.9 | RAS-5WHNPE / RWM-5.0NE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.3 | 0.21 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 8.6 | 5.96 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1508 | Hitachi | Yutaki S 6.0 HP 410A | RAS-6WHVNPE / RWM-6.0NE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.5 | 12.31 | 53.5 | 12.31 | RAS-6WHVNPE / RWM-6.0NE | Heat pump |  | 27.4 | 6.3 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25 | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.3 | 0.07 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-12 | EN 61000-3-11 |  |  | No | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 25.8 | 5.93 | [9 empty] | No |  | No | Yes |  |  |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
HP_1509 | Hitachi | Yutaki S 6.0 HP 3Ph | RAS-6WHNPE / RWM-6.0NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.3 | 16.14 | 23.3 | 16.14 | RAS-6WHNPE / RWM-6.0NE | Heat pump |  | 14.4 | 9.98 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.3 | 0.21 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 8.6 | 5.96 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1510 | Hitachi | Yutaki Monobloc 5 HP R410A | RASM-5VNE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.72 | 6.38 | 27.72 | 6.38 | RASM5-VNE | Heat pump |  | 27.72 | 6.38 | ECML0133 A_r2-YUTAKI M 2016.pdf | ECML0133 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | Yes | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 24 | 0.153 | 0.346 | Requires Zsource ≤Zmax | 0.24 | No |  |  | No |  |  | Yes | No | 13
HP_1511 | Hitachi | Yutaki Monobloc 6 HP R410A | RASM-6VNE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.72 | 6.38 | 27.72 | 6.38 | RASM6-VNE | Heat pump |  | 27.72 | 6.38 | ECML0133 A_r2-YUTAKI M 2016.pdf | ECML0133 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | Yes | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 24 | 0.153 | 0.346 | Requires Zsource ≤Zmax | 0.24 | No |  |  | No |  |  | Yes | No | 13
HP_1512 | Hitachi | Yutaki Monobloc 3 HP R410A | RASM-3VNE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.53 | 4.49 | 19.53 | 4.49 | RASM3-VNE | Heat pump |  | 19.53 | 4.49 | ECML0133 A_r2-YUTAKI M 2016.pdf | ECML0133 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | Yes | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 24 | 0.108 | 0.491 | Requires Zsource ≤Zmax | 0.35 | No |  |  | No |  |  | Yes | No | 13
HP_1513 | Hitachi | Yutaki Monobloc 4 HP R410A | RASM-4VNE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.72 | 6.38 | 27.72 | 6.38 | RASM4-VNE | Heat pump |  | 27.72 | 6.38 | ECML0133 A_r2-YUTAKI M 2016.pdf | ECML0133 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | Yes | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 24 | 0.153 | 0.346 | Requires Zsource ≤Zmax | 0.24 | No |  |  | No |  |  | Yes | No | 13
HP_1514 | Hitachi | Yutaki Monobloc 4 HP (3P) R410A | RASM-4NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 12.87 | 8.92 | 12.87 | 8.92 | RASM-4NE | Heat pump |  | 12.87 | 8.88 | ECML0133 A_r2-YUTAKI M 2016.pdf | ECML0133 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
HP_1515 | Hitachi | Yutaki Monobloc 5 HP (3P) R410A | RASM-5NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 12.87 | 8.92 | 12.87 | 8.92 | RASM-5NE | Heat pump |  | 12.87 | 8.88 | ECML0133 A_r2-YUTAKI M 2016.pdf | ECML0133 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
HP_1516 | Hitachi | Yutaki Monobloc 6 HP (3P) R410A | RASM-6NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 14.67 | 10.16 | 14.67 | 10.16 | RASM-6NE | Heat pump |  | 14.67 | 10.12 | ECML0133 A_r2-YUTAKI M 2016.pdf | ECML0133 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
HP_1517 | Hitachi | Yutaki Monobloc 2 HP R32 | RASM-2VRE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 9.54 | 2.19 | 9.54 | 2.19 | RASM-2VRE | Heat pump |  | 9.54 | 2.19 | ECML0182 A_r0-YUTAKI M R32 | ECML0182 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
HP_1518 | Hitachi | Yutaki S Combi 2 HP R32 | RAS-2WHVRP / RWD-2.0NRWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 33.7 | 7.75 | 33.7 | 7.75 | RAS-2WHVRP | Heat pump |  | 9.4 | 2.16 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWD-2.0NRWE-(200/260)S-K | Heat pump |  | 0.2 | 0.05 | ECML0185 A_r0-YUTAKI SCombi R32 | ECML0185 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1519 | Hitachi | Yutaki S Combi 2 HP R410A | RAS-2WHVNP / RWD-2.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 36.7 | 8.44 | 36.7 | 8.44 | RAS-2WHVNP | Heat pump |  | 12.4 | 2.16 | 17F20445xA_r0_RAS-WHNP | 17F20445xA | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWD-2.0NWE-(200/260)S-K | Heat pump |  | 0.2 | 0.05 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1520 | Hitachi | Yutaki S Combi 2.5 HP R32 | RAS-2.5WHVRP / RWD-2.5NRWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 35.97 | 8.27 | 35.97 | 8.27 | RAS-2.5WHVRP | Heat pump |  | 11.67 | 2.67 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWD-2.5NRWE-(200/260)S-K | Heat pump |  | 0.2 | 0.05 | ECML0185 A_r0-YUTAKI SCombi R32 | ECML0185 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1521 | Hitachi | Yutaki S Combi 2.5 HP R410A | RAS-2.5WHVNP / RWD-2.5NWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 38.5 | 8.86 | 38.5 | 8.86 | RAS-2.5WHVNP | Heat pump |  | 14.2 | 3.27 | 17F20445xA_r0_RAS-WHNP | 17F20445xA | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWD-2.5NWE-(200/260)S-K | Heat pump |  | 0.2 | 0.05 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1522 | Hitachi | Yutaki S Combi 3 HP R32 | RAS-3WHVRP / RWD-3.0NRWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 38.5 | 8.86 | 38.5 | 8.86 | RAS-3WHVRP | Heat pump |  | 14.2 | 3.27 | A10074490A_r0-RAS-3WHVRP and A10075160A_r0(PED)-RAS-3WHVRP | A10074490A | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWD-3.0NRWE-(200/260)S-K | Heat pump |  | 0.2 | 0.05 | ECML0185 A_r0-YUTAKI SCombi R32 | ECML0185 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1523 | Hitachi | Yutaki S Combi 3 HP R410A | RAS-3WHVNP / RWD-3.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 40.3 | 9.27 | 40.3 | 9.27 | RAS-3WHVNP | Heat pump |  | 16 | 3.68 | 17F20445xA_r0_RAS-WHNP | 17F20445xA | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWD-3.0NWE-(200/260)S-K | Heat pump |  | 0.2 | 0.05 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1524 | Hitachi | Yutaki S Combi 4 HP R410A | RAS-4WHVNPE / RWD-4.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 64.8 | 14.9 | 64.8 | 14.9 | RAS-4WHVNPE | Heat pump |  | 27.4 | 6.3 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25 | No |  |  | No |  |  | No
[16 empty] | RWD-4.0NWE-(200/260)S-K | Heat pump |  | 0.3 | 0.07 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 25.8 | 5.93 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.3 | 2.6 | [17 empty] | N/A | N/A | N/A
HP_1525 | Hitachi | Yutaki S Combi 5 HP R410A | RAS-5WHVNPE / RWD-5.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 64.8 | 14.9 | 64.8 | 14.9 | RAS-5WHVNPE | Heat pump |  | 27.4 | 6.3 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25 | No |  |  | No |  |  | No
[16 empty] | RWD-5.0NWE-(200/260)S-K | Heat pump |  | 0.3 | 0.07 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 25.8 | 5.93 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.3 | 2.6 | [17 empty] | N/A | N/A | N/A
HP_1526 | Hitachi | Yutaki S Combi 6 HP R410A | RAS-6WHVNPE / RWD-6.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 64.8 | 14.9 | 64.8 | 14.9 | RAS-6WHVNPE | Heat pump |  | 27.4 | 6.3 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25 | No |  |  | No |  |  | No
[16 empty] | RWD-6.0NWE-(200/260)S-K | Heat pump |  | 0.3 | 0.07 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18 | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 25.8 | 5.93 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.3 | 2.6 | [17 empty] | N/A | N/A | N/A
HP_1527 | Hitachi | Yutaki S 8 HP 410A 3Ph | RAS-8WHNPE / RWM-8.0NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 35 | 24.25 | 35 | 24.25 | RAS-8WHNPE | Heat pump |  | 21.6 | 14.9 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | Not Applicable | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | Yes | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWM-8.0NE | Back-up heater - on-board |  | 13.4 | 9.25 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1528 | Hitachi | Yutaki S 10 HP 410A 3Ph | RAS-10WHNPE / RWM-10.0NE | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 35 | 24.25 | 35 | 24.25 | RAS-10WHNPE | Heat pump |  | 21.6 | 14.9 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | Not Applicable | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | No | Yes | No | No | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[16 empty] | RWM-10.0NE | Back-up heater - external |  | 13.4 | 9.25 | ECML0126 A_r3-YUTAKI S 2016 | ECML0126 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1529 | Hitachi | Yutaki Monobloc 3 HP R32 | RASM-3VRE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | RASM-3VRE | Heat pump |  | 16 | 3.68 | ECML0183 A_r2-YUTAKI M R32(3HP) | ECML0183 A_r2 | EN 61000-3-2 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | No | No | No | Yes | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.43 | No |  |  | No |  |  | Yes | No | 13
HP_1530 | Hitachi | Yutaki S 2 HP R32 | RAS-2WHVRP / RWM-2.0NRE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 22.5 | 5.18 | 22.5 | 5.18 | RAS-2WHVRP / RWM-2.0NRE | Heat pump |  | 9.4 | 2.16 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.2 | 0.05 | ECML0184 A_r0-YUTAKI S R32 | ECML0184 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1531 | Hitachi | Yutaki S 2.5 HP R32 | RAS-2.5WHVRP / RWM-2.5NRE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.7 | 5.68 | 24.7 | 5.68 | RAS-2.5WHVRP / RWM-2.5NRE | Heat pump |  | 11.6 | 2.67 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.2 | 0.05 | ECML0184 A_r0-YUTAKI S R32 | ECML0184 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1532 | Hitachi | Yutaki S 3 HP R32 | RAS-3WHVRP / RWM-3.0NRE | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.3 | 6.28 | 27.3 | 6.28 | RAS-3WHVRP / RWM-3.0NRE | Heat pump |  | 14.2 | 3.27 | A10074490A_r0-RAS-3WHVRP and A10075160A_r0(PED)-RAS-3WHVRP | A10074490A | EN 61000-3-2 | EN 61000-3-11 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | No | No | No | Yes | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.43 | No |  |  | No |  |  | No
[17 empty] | Heat pump |  | 0.2 | 0.05 | ECML0184 A_r0-YUTAKI S R32 | ECML0184 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | Yes | No | 13
[17 empty] | Back-up heater - on-board |  | 12.9 | 2.97 | [9 empty] | Yes |  | No | Yes |  |  |  |  | N/A | N/A | N/A
HP_1533 | Hitachi | Yutaki S Combi 4 HP R410A | RAS-4WHNPE / RWD-4.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 32.7 | 22.66 | 32.7 | 22.66 | RAS-4WHNPE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | RWD-4.0NWE-(200/260)S-K | Heat pump |  | 0.3 | 0.21 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 8.6 | 5.93 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1534 | Hitachi | Yutaki S Combi 6 HP R410A | RAS-6WHNPE / RWD-6.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 34.5 | 23.9 | 34.5 | 23.9 | RAS-6WHNPE | Heat pump |  | 14.4 | 9.98 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | RWD-6.0NWE-(200/260)S-K | Heat pump |  | 0.3 | 0.21 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 8.6 | 5.93 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1535 | Hitachi | Yutaki S Combi 5 HP R410A | RAS-5WHNPE / RWD-5.0NWE-(200/260)S-K | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 32.7 | 22.66 | 32.7 | 22.66 | RAS-5WHNPE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM & FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | No | No | Yes | YUTAKI HARM & FLICK(2019 Status).xlsx | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
[16 empty] | RWD-5.0NWE-(200/260)S-K | Heat pump |  | 0.3 | 0.21 | ECML0131 A_r3-YUTAKI SCOMBI 2016 | ECML0131 | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
[17 empty] | Back-up heater - on-board |  | 8.6 | 5.93 | [17 empty] | N/A | N/A | N/A
[17 empty] | Water (immersion) heater - on-board |  | 11.2 | 2.58 | [17 empty] | N/A | N/A | N/A
HP_1536 | Hitachi | Yutaki S Combi 2 HP R32 | RAS-2WHVRP1 / RWD-2.0RW1E-220S(-K) | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 34.96 | 8.04 | 34.96 | 8.04 | RAS-2WHVRP1 | Heat pump |  | 9.36 | 2.15 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWD-2.0RW1E-220S(-K) | Back-up heater - on-board |  | 13.6 | 3.13 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.29
[17 empty] | Water (immersion) heater - on-board |  | 12 | 2.76 | [17 empty] | N/A | N/A | N/A
HP_1537 | Hitachi | Yutaki S Combi 2.5 HP R32 | RAS-2.5WHVRP1 / RWD-2.5RW1E-220S(-K) | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 37.21 | 8.56 | 37.21 | 8.56 | RAS-2.5WHVRP1 | Heat pump |  | 11.61 | 2.67 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWD-2.5RW1E-220S(-K) | Back-up heater - on-board |  | 13.6 | 3.13 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.29
[17 empty] | Water (immersion) heater - on-board |  | 12 | 2.76 | [17 empty] | N/A | N/A | N/A
HP_1538 | Hitachi | Yutaki S Combi 3 HP R32 | RAS-3WHVRP1 / RWD-3.0RW1E-220S(-K) | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 39.82 | 9.16 | 39.82 | 9.16 | RAS-3WHVRP1 | Heat pump |  | 14.22 | 3.27 | A10074490A_r0-RAS-3WHVRP and A10075160A_r0(PED)-RAS-3WHVRP | A10074490A | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xlsx |  | Yes | No | No | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.42
[16 empty] | RWD-3.0RW1E-220S(-K) | Back-up heater - on-board |  | 13.6 | 3.13 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.29
[17 empty] | Water (immersion) heater - on-board |  | 12 | 2.76 | [17 empty] | N/A | N/A | N/A
HP_1539 | Hitachi | Yutaki S Combi 4 HP | RAS-4WHVNPE / RWD-4.0NW1E-220S(-K) | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 66.15 | 15.21 | 66.15 | 15.21 | RAS-4WHVNPE | Heat pump |  | 27.45 | 6.31 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM FLICK(2019 Status).xslx |  | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25
[16 empty] | RWD-4.0NW1E-220S(-K) | Back-up heater - on-board |  | 26 | 6 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xslx |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.19
[17 empty] | Water (immersion) heater - on-board |  | 12.7 | 2.9 | [17 empty] | N/A | N/A | N/A
HP_1540 | Hitachi | Yutaki S Combi 5 HP | RAS-5WHVNPE / RWD-5.0NW1E-220S(-K) | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 66.15 | 15.21 | 66.15 | 15.21 | RAS-5WHVNPE | Heat pump |  | 27.45 | 6.31 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM FLICK(2019 Status).xslx |  | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25
[16 empty] | RWD-5.0NW1E-220S(-K) | Back-up heater - on-board |  | 26 | 6 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xslx |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.19
[17 empty] | Water (immersion) heater - on-board |  | 12.6 | 2.9 | [17 empty] | N/A | N/A | N/A
HP_1541 | Hitachi | Yutaki S Combi 6 HP | RAS-6WHVNPE / RWD-6.0NW1E-220S(-K) | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 66.15 | 15.21 | 66.15 | 15.21 | RAS-6WHVNPE | Heat pump |  | 27.45 | 6.31 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM FLICK(2019 Status).xslx |  | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25
[16 empty] | RWD-6.0NW1E-220S(-K) | Back-up heater - on-board |  | 26 | 6 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xslx |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.19
[17 empty] | Water (immersion) heater - on-board |  | 12.6 | 2.9 | [17 empty] | N/A | N/A | N/A
HP_1542 | Hitachi | Yutaki S Combi 4 HP | RAS-4WHNPE / RWD-4.0NW1E-220S(-K) | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13.04 | 21.63 | 30.6 | 21.63 | RAS-4WHNPE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xslx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWD-4.0NW1E-220S(-K) | Back-up heater - on-board |  | 18 | 4.14 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - on-board |  | 12.6 | 2.9 | [17 empty] | N/A | N/A | N/A
HP_1543 | Hitachi | Yutaki S Combi 5 HP | RAS-5WHNPE / RWD-5.0NW1E-220S(-K) | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13.04 | 21.63 | 30.6 | 21.63 | RAS-5WHNPE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xslx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWD-5.0NW1E-220S(-K) | Back-up heater - on-board |  | 18 | 4.14 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - on-board |  | 12.6 | 2.9 | [17 empty] | N/A | N/A | N/A
HP_1544 | Hitachi | Yutaki S Combi 6 HP | RAS-6WHNPE / RWD-6.0NW1E-220S(-K) | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 13.04 | 23.43 | 32.4 | 23.43 | RAS-6WHNPE | Heat pump |  | 14.4 | 9.98 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xslx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWD-6.0NW1E-220S(-K) | Back-up heater - on-board |  | 18 | 4.14 | UKEN0001 A_r0-YUTAKI SCOMBI 220L | UKEN0001_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Water (immersion) heater - on-board |  | 12.6 | 2.9 | [17 empty] | N/A | N/A | N/A
HP_1545 | Hitachi | Yutaki S 2 HP R32 | RAS-2WHVRP1 / RWM-2.0R1E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 23.06 | 5.3 | 23.06 | 5.3 | RAS-2WHVRP1 / RWM-2.0R1E | Heat pump |  | 9.36 | 2.15 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13.7 | 3.15 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-2 | EN 61000-3-3 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | #REF! |  | #REF! | #REF! |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1546 | Hitachi | Yutaki S 2.5 HP R32 | RAS-2.5WHVRP1 / RWM-2.5R1E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25.31 | 5.82 | 25.31 | 5.82 | RAS-2.5WHVRP1 / RWM-2.5R1E | Heat pump |  | 11.61 | 2.67 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13.7 | 3.15 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-2 | EN 61000-3-3 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | #REF! |  | #REF! | #REF! |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1547 | Hitachi | Yutaki S 3.0 HP R32 | RAS-3.0WHVRP1 / RWM-3.0R1E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.92 | 6.42 | 27.92 | 6.42 | RAS-3.0WHVRP1 / RWM-3.0R1E | Heat pump |  | 14.22 | 3.27 | 17F25488xA_r1_RAS-(2-2.5)WHVRP | 17F25488 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xlsx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13.7 | 3.15 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-2 | EN 61000-3-3 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | #REF! |  | #REF! | #REF! |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1548 | Hitachi | Yutaki S 4 HP | RAS-4WHVNPE / RWM-4.0N1E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 54.15 | 12.45 | 54.15 | 12.45 | RAS-4WHVNPE | Heat pump |  | 27.45 | 6.31 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 A_r2 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25
[16 empty] | RWM-4.0N1E | Back-up heater - on-board |  | 26.7 | 6.14 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xslx |  | Yes | No | Yes | #REF! |  | #REF! | #REF! |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28
HP_1549 | Hitachi | Yutaki S 5 HP | RAS-5WHVNPE / RWM-5.0N1E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 54.15 | 12.45 | 54.15 | 12.45 | RAS-5WHVNPE | Heat pump |  | 27.45 | 6.31 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 A_r2 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25
[16 empty] | RWM-5.0N1E | Back-up heater - on-board |  | 26.7 | 6.14 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xslx |  | Yes | No | Yes | #REF! |  | #REF! | #REF! |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28
HP_1550 | Hitachi | Yutaki S 6 HP | RAS-6WHVNPE / RWM-6.0N1E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 54.15 | 12.45 | 54.15 | 12.45 | RAS-6WHVNPE | Heat pump |  | 27.45 | 6.31 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 A_r2 | EN 61000-3-12 | EN 61000-3-11 | YUTAKI HARM FLICK(2019 Status).xlsx |  | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.119 | 0.442 | Requires Zsource ≤Zmax | 0.25
[16 empty] | RWM-6.0N1E | Back-up heater - on-board |  | 26.7 | 6.14 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-12 | EN 61000-3-11 | Harmonics & Flicker YUT S & SC.xslx |  | Yes | No | Yes | #REF! |  | #REF! | #REF! |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.28
HP_1551 | Hitachi | Yutaki S 4 HP | RAS-4WHNPE / RWM-4.0N1E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21.9 | 15.17 | 21.9 | 15.17 | RAS-4WHNPE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xslx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWM-4.0N1E | Back-up heater - on-board |  | 9.3 | 6.44 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-2 | EN 61000-3-3 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | #REF! |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1552 | Hitachi | Yutaki S 5 HP | RAS-5WHNPE / RWM-5.0N1E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21.9 | 15.17 | 21.9 | 15.17 | RAS-5WHNPE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xslx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWM-5.0N1E | Back-up heater - on-board |  | 9.3 | 6.44 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-2 | EN 61000-3-3 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | #REF! |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1553 | Hitachi | Yutaki S 6 HP | RAS-6WHNPE / RWM-6.0N1E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21.9 | 15.17 | 21.9 | 15.17 | RAS-6WHNPE | Heat pump |  | 12.6 | 8.73 | ECML0132 A_r2-RAS-WHNPE 2016 | ECML0132 | EN 61000-3-2 | EN 61000-3-3 | YUTAKI HARM FLICK(2019 Status).xslx |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | RWM-6.0N1E | Back-up heater - on-board |  | 9.3 | 6.44 | UKEN0002 A_r0-YUTAKI S (R1E - N1E) | UKEN0002_r0 | EN 61000-3-2 | EN 61000-3-3 | Harmonics & Flicker YUT S & SC.xlsx |  | Yes | Yes | Yes | #REF! |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1601 | Clausius | HC 3-15 | Clausius HC 3-15 | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | Clausius H 3-15 | Heat pump |  | 26 | 6.29 | Declaración de conformidad.pdf | Mod. 078.1 | EN 61000-3-12 | EN 61000-3-11 | TEST REPORT Clausius HEAT PUMPS V.4_1.pdf | ver. 1.0 | No | No | No | No | Yes | No | Yes | Conformidad EMC domésticas.pdf | Equipment complying with IEC 61000-3-12 |  |  | 31 | 0.185 | 0.285 | Requires Zsource ≤Zmax | 0.217 | Yes | No |  | Yes | No |  | Yes | No
HP_1602 | Clausius | H 3-15 | Clausius H 3-15 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | Clausius H 3-15 | Heat pump |  | 26 | 6.29 | Declaración de conformidad.pdf | Mod. 078.1 | EN 61000-3-12 | EN 61000-3-11 | TEST REPORT Clausius HEAT PUMPS V.4_1.pdf | ver. 1.0 | No | No | No | No | Yes | No | Yes | Conformidad EMC domésticas.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.217 | Yes | No |  | Yes | No |  | Yes | No
HP_1603 | Clausius | 5-25 | Clausius HC 5-25 | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 27.35 | 6.29 | 27.35 | 6.29 | Clausius H 5-25 | Heat pump |  | 27.35 | 6.29 | Declaración de conformidad.pdf | Mod. 078.1 | EN 61000-3-12 | EN 61000-3-11 | TEST REPORT Clausius HEAT PUMPS V.4_1.pdf | ver. 1.0 | No | No | No | No | Yes | No | Yes | Declaración de conformidad.pdf | Equipment complying with IEC 61000-3-12 |  |  | 27 | 0.161 | 0.328 | Requires Zsource ≤Zmax | 0.2169 | Yes | No |  | Yes | No |  | Yes | No
HP_1604 | Clausius | 5-25 | Clausius H 5-25 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 27.35 | 6.29 | 27.35 | 6.29 | Clausius H 5-25 | Heat pump |  | 27.35 | 6.29 | Declaración de conformidad.pdf | Mod. 078.1 | EN 61000-3-12 | EN 61000-3-11 | TEST REPORT Clausius HEAT PUMPS V.4_1.pdf | ver. 1.0 | No | No | No | No | Yes | No | Yes | Declaración de conformidad.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.2169 | Yes | No |  | Yes | No |  | Yes | No
HP_1605 | Clausius | HC 1-10 | Clausius HC 1-10 | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 22.9 | 5.27 | 22.9 | 5.27 | Clausius H 1-10 | Heat pump |  | 22.9 | 5.27 | Declaración de conformidad.pdf | Mod. 078.1 | EN 61000-3-12 | EN 61000-3-11 | TEST REPORT Clausius HEAT PUMPS V.4_1.pdf | ver. 1.0 | No | No | No | No | Yes | No | Yes | Conformidad EMC domésticas.pdf | Equipment complying with IEC 61000-3-12 |  |  | 25 | 0.132 | 0.402 | Requires Zsource ≤Zmax | 0.217 | Yes | No |  | Yes | No |  | Yes | No
HP_1606 | Clausius | H 1-10 | Clausius H 1-10 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 22.9 | 5.27 | 22.9 | 5.27 | Clausius H 1-10 | Heat pump |  | 22.9 | 5.27 | Declaración de conformidad.pdf | Mod. 078.1 | EN 61000-3-12 | EN 61000-3-11 | TEST REPORT Clausius HEAT PUMPS V.4_1.pdf | ver. 1.0 | No | No | No | No | Yes | No | Yes | Conformidad EMC domésticas.pdf | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.217 | Yes | No |  | Yes | No |  | Yes | No
HP_1607 | Clausius | HC 5-25 | Clausius HC 5-25 | Heating & Cooling | Ground Source | 3 | 400 |  |  |  |  | 20 | 13.86 | 20 | 13.86 | Clausius HC 5-25 | Heat pump |  | 20 | 13.9 | Declaración de conformidad.pdf | Mod.078.1 | EN 61000-3-12 | EN 61000-3-11 | TEST REPORT Clausius 5-25 3Ph.pdf |  | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.4157 | 0.385 | Requires Zsource ≤Zmax | 0.3
HP_1701 | SOLECO | RM2 | SOL12-3 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 8 | 5.54 | 8 | 5.54 | 902957-02 | Heat pump |  | 8 | 5.52 | EC Declaration Of Conformity Seleco RM2 | DOC CE RM2 12-3 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Form A Seleco RM2 12-3pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No |  | No | No |  | No | No
HP_1702 | SOLECO | RM2 | SOL18-3 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | 902958-02 | Heat pump |  | 10 | 6.9 | EC Declaration Of Conformity Seleco RM2 | DOC CE RM2 18-3 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Form A Seleco RM2 18-3pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No |  | No | No |  | No | No
HP_1703 | SOLECO | RM2 | SOL26-3 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 15 | 10.39 | 15 | 10.39 | 902959-02 | Heat pump |  | 15 | 10.4 | EC Declaration Of Conformity Seleco RM2 | DOC CE RM2 26-3 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Form A Seleco RM2 26-3pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No |  | No | No |  | No | No
HP_1801 | Earth Save Products | Varimax 12 | H8A | Heating only | Air Source | 1 | 230 |  |  |  |  | 12 | 2.76 | 12 | 2.76 | Varimax 12 | Heat pump |  | 12 | 2.76 | Varimax 12 Test Certificate | GZEM1512006472HSV | EN 61000-3-2 | EN 61000-3-3 | Varimax 12 Test Report | GZEM151200647201 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No | No | 0 | No | No | 0 | No | No | 0
HP_1802 | Earth Save Products | Solis 17kW | Solis 17kW | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.5 | 3.57 | 15.5 | 3.57 | Solis 17 | Heat pump |  | 15.5 | 3.57 | EMC Certificate Solis Units | E8A191204840002 | EN 61000-3-2 | EN 61000-3-3 | EMC Test Reports Solis Units | 64.711.19.00146.01-E | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not Applicable |  |  | N/A | N/A | N/A | Not Applicable |  | No | No | 0 | No | No | 0 | No | No | 0
HP_1803 | Earth Save Products | Solis 11kW | Solis 11kW | Heating only | Air Source | 1 | 230 |  |  |  |  | 11.2 | 2.58 | 11.2 | 2.58 | Solis 11kW | Heat pump |  | 11.2 | 2.58 | EMC Certificate Solis Units | E8A191204840002 | EN 61000-3-2 | EN 61000-3-3 | 64.711.19.00146.01 TRF EMC | 64.711.19.00146.01-E | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not Applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No | 0 | No | No | 0 | No | No | 0
HP_1901 | Enertech | GSi12 | CTC GSi 12 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 49 | 11.27 | 49 | 11.27 | CTC GSi 12 1x230V | Whole system |  | 49 | 11.27 | 16220589-1-EU DoC CTC GSi 12 GSi 16-en | 162 205 89-1 | EN 61000-3-12 | EN 61000-3-11 | 19035-HF Harmonics and Flicker Enertech AB, GSI12 1x230V | 19035-05H | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 31 | 0.17825 | 0.29677 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1902 | Enertech | EcoPart 425 | CTC EcoPart 425 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 54.8 | 12.6 | 54.8 | 12.6 | CTC EcoPart 425 | Heat pump |  | 54.8 | 12.6 | 16220521 EU DoC CTC EcoPart 425-435 | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 19126-HF Harmonics and Flicker Enertech AB, EcoPart 425 | 19126-HF | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.2143 | 0.2469 | Requires Zsource ≤Zmax | 0.349 | No |  |  | No |  |  | No
HP_1903 | Enertech | EcoPart 425 | CTC EcoPart i425 Pro | Heating only | Ground Source | 1 | 230 |  |  |  |  | 58.8 | 13.52 | 58.8 | 13.52 | CTC EcoPart i425 Pro | Heat pump |  | 58.8 | 13.52 | 16220521 EU DoC CTC EcoPart 425-435 | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 19126-HF Harmonics and Flicker Enertech AB, EcoPart 425 | 19126-HF | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 17 | 0.2143 | 0.2469 | Requires Zsource ≤Zmax | 0.349 | No |  |  | No |  |  | No
HP_1904 | Enertech | EcoPart | CTC EcoPart 406 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 14 | 3.22 | 14 | 3.22 | CTC EcoPart 406 | Heat pump |  | 14 | 2.7 | 16220579-2-EU DoC CTC EcoPart 400-en | 162 205 79-2 | EN 61000-3-2 | EN 61000-3-3 | 19130-HF Harmonics and Flicker Enertech AB, EcoPart 406 | 19130-HF | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1905 | Enertech | EcoPart | CTC EcoPart 410 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 21.6 | 4.968 | 21.6 | 4.968 | CTC EcoPart 410 | Heat pump |  | 21.6 | 4.4 | 16220579-2-EU DoC CTC EcoPart 400-en | 162 205 79-2 | EN 61000-3-12 | EN 61000-3-11 | 19129-HF Harmonics and Flicker Enertech AB, EcoPart 410 | 19129-HF | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.409 | No |  |  | No |  |  | No
HP_1906 | Enertech | EcoPart | CTC EcoPart 414 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 33.2 | 7.636 | 33.2 | 7.636 | CTC EcoPart 414 | Heat pump |  | 33.2 | 6.3 | 16220579-2-EU DoC CTC EcoPart 400-en | 162 205 79-2 | EN 61000-3-12 | EN 61000-3-11 | 19128-HF Harmonics and Flicker Enertech AB, EcoPart 414 | 19128-HF | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.349 | No |  |  | No |  |  | No
HP_1907 | Enertech | EcoPart 430 | CTC EcoPart 430 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 66.4 | 15.27 | 66.4 | 15.27 | CTC EcoPart 430 | Heat pump |  | 66.4 | 15.27 | 16220521 EU DoC CTC EcoPart 425-435 | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 19127-HF Harmonics and Flicker Enertech AB, EcoPart 430 | 19127-HF | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.35126 | 0.1506 | Requires Zsource ≤Zmax | 0.349 | No |  |  | No |  |  | No
HP_1908 | Enertech | EcoPart 430 | CTC EcoPart i430 Pro | Heating only | Ground Source | 1 | 230 |  |  |  |  | 70.4 | 16.19 | 70.4 | 16.19 | CTC EcoPart i430 Pro | Heat pump |  | 70.4 | 16.19 | 16220521 EU DoC CTC EcoPart 425-435 | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 19127-HF Harmonics and Flicker Enertech AB, EcoPart 430 | 19127-HF | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.35126 | 0.1506 | Requires Zsource ≤Zmax | 0.349 | No |  |  | No |  |  | No
HP_1909 | Enertech | EcoPart | CTC EcoPart 412 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 27.1 | 6.233 | 27.1 | 6.233 | CTC EcoPart 412 | Heat pump |  | 27.1 | 5.2 | 16220579-2-EU DoC CTC EcoPart 400-en | 162 205 79-2 | EN 61000-3-12 | EN 61000-3-11 | 19112-HF Harmonics and Flicker Enertech AB, EcoPart 412 | 19112-HF | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.347 | No |  |  | No |  |  | No
HP_1910 | Enertech | EcoPart | CTC EcoPart 408 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 19.5 | 4.485 | 19.5 | 4.485 | CTC EcoPart 408 | Heat pump |  | 19.5 | 3.4 | 16220579-2-EU DoC CTC EcoPart 400-en | 162 205 79-2 | EN 61000-3-12 | EN 61000-3-11 | 19131-HF Harmonics and Flicker Enertech AB, EcoPart 408 | 19131-HF | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36 | No |  |  | No |  |  | No
HP_1911 | Enertech | EcoAir | CTC EcoAir 510M | Heating only | Air Source | 1 | 230 |  |  |  |  | 20.8 | 4.78 | 20.8 | 4.78 | CTC EcoAir 510M | Heat pump |  | 20.8 | 4.78 | 16220517-2-EU DoC CTC EcoAir 510M 230V-en | 162 205 17-2 | EN 61000-3-12 | EN 61000-3-11 | 19012 Rev 1 Signed report Enertech EcoAir 510M | 19012 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 23 | 0.1103 | 0.4808 | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1912 | Enertech | GSi | CTC GSi 8 3x400V | Heating only | Ground Source | 3 | 400 |  |  |  |  | 13.3 | 9.2145 | 13.3 | 9.2145 | CTC GSi 8 3x400V | Whole system |  | 13.3 | 8.9 | 16230553-2-EU DoC CTC GSi-en | 162 305 53-2 | EN 61000-3-2 | EN 61000-3-3 | 20019-HF Harmonics and Flicker Enertech AB, GSi8 | 20019-HF | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1913 | Enertech | GS 600 | CTC GS 606 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 39.4 | 9.062 | 39.4 | 9.062 | CTC GS 606 1x230V | Whole system |  | 39.4 | 8.5 | 16230578-1-EU DoC CTC GS 606-608-1x230V-en | 16230578-1 | EN 61000-3-12 | EN 61000-3-11 | 19095-HF Harmonics and Flicker Enertech AB, GS606 | 19095-03 HF | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1914 | Enertech | GS 600 | CTC GS 608 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 45.6 | 10.488 | 45.6 | 10.488 | CTC GS 608 1x230V | Whole system |  | 45.6 | 9.7 | 16230578-1-EU DoC CTC GS 606-608-1x230V-en | 16230578-1 | EN 61000-3-12 | EN 61000-3-11 | 19094-HF Harmonics and Flicker Enertech AB, GS608 | 19094-02H | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1915 | Enertech | EcoHeat | EcoHeat 406 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 52.13 | 11.9899 | 52.13 | 11.9899 | EcoHeat 406 | Whole system |  | 52.13 | 11.7 | 16220513-2-EU DoC CTC EcoHeat 400-en | 16220513 | EN 61000-3-2 | EN 61000-3-3 | 19132-HF Harmonics and Flicker Enertech AB, EcoHeat 406 | 19132-HF | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1916 | Enertech | EcoHeat | CTC EcoHeat 408 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 57.63 | 13.25 | 57.63 | 13.25 | EcoHeat 408 | Whole system |  | 57.63 | 13.25 | 16220513-3-EU DoC CTC EcoHeat 400 | 16220513 | EN 61000-3-12 | EN 61000-3-11 | 19133-HF Harmonics and Flicker Enertech AB, EcoHeat 408 | 19133-HF | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1917 | Enertech | EcoHeat | CTC EcoHeat 410 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 59.73 | 13.74 | 59.73 | 13.74 | EcoHeat 410 | Whole system |  | 59.73 | 13.74 | 16220513-3-EU DoC CTC EcoHeat 400 | 16220513 | EN 61000-3-12 | EN 61000-3-11 | 20066-HF Harmonics and Flicker Enertech AB, EcoHeat 410 | 20066-HF | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.392 | No |  |  | No |  |  | No
HP_1918 | Enertech | EcoHeat | CTC EcoHeat 412 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 62.2 | 14.31 | 62.2 | 14.31 | EcoHeat 412 | Whole system |  | 62.2 | 14.31 | 16220513-3-EU DoC CTC EcoHeat 400 | 16220513 | EN 61000-3-12 | EN 61000-3-11 | 20067-HF Harmonics and Flicker Enertech AB, EcoHeat 412 | 20067-HF | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.341 | No |  |  | No |  |  | No
HP_1919 | Enertech | EcoAir | CTC EcoAir 610M | Heating only | Air Source | 3 | 400 |  |  |  |  | 7.1 | 4.919 | 7.1 | 4.919 | EcoAir 610M | Whole system |  | 7.1 | 4.9 | 16220578-2-EU DoC CTC EcoAir 610M-614M-en | 16220578 | EN 61000-3-2 | EN 61000-3-3 | 17127 Rev1 Signed report Enertech, EcoAir 610M_614M | 17127 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1920 | Enertech | EcoAir | CTC EcoAir 614M | Heating only | Air Source | 3 | 400 |  |  |  |  | 10.2 | 7.0668 | 10.2 | 7.0668 | EcoAir 614M | Whole system |  | 10.2 | 7.1 | 16220578-2-EU DoC CTC EcoAir 610M-614M-en | 16220578 | EN 61000-3-2 | EN 61000-3-3 | 17127 Rev1 Signed report Enertech, EcoAir 610M_614M | 17127 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1921 | Enertech | EcoAir | CTC EcoAir 622M | Heating only | Air Source | 3 | 400 |  |  |  |  | 16.9 | 11.7087 | 16.9 | 11.7087 | EcoAir 622M | Whole system |  | 16.9 | 11.7 | 16230569-1-EU DoC CTC EcoAir 622M-en | 16230569 | EN 61000-3-12 | EN 61000-3-11 | 17105-HF Harmonics and Flicker Enertech AB, EcoAir 622M | 17105-HF | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1405 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_1922 | Enertech | CombiAir | CTC Enertech CombiAir 6M | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15 | 3.45 | 15 | 3.45 | CTC Enertech CombiAir 6M | Whole system |  | 15 | 3.45 | 16230593-1-EU DoC CTC CombiAir 6M-en | 16230593-1 | EN 61000-3-2 | EN 61000-3-3 | 330609 TRF EMC | E17201.00 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1923 | Enertech | CombiAir | CTC Enertech CombiAir 8M | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | CTC Enertech CombiAir 8M | Whole system |  | 16 | 3.68 | 16230594-1-EU DoC CTC CombiAir 8M-en | 16230594-1 | EN 61000-3-2 | EN 61000-3-3 | EMC TEST REPORT 13028940 Ed1 20013-09-02 | 13028940 Ed 1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_1924 | Enertech | CombiAir | CTC Enertech CombiAir 12M | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 23 | 5.29 | 23 | 5.29 | CTC Enertech CombiAir 12M | Whole system |  | 23 | 5.29 | 16230595-1-EU DoC CTC CombiAir 12M-en | 16230595-1 | EN 61000-3-12 | EN 61000-3-11 | EMC TEST REPORT 1216141D Ed2 | 1216141D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_1925 | Enertech | CombiAir | CTC Enertech CombiAir 16M | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | CTC Enertech CombiAir 16M | Whole system |  | 25 | 5.75 | 16240509-1-EU DoC CTC CombiAir 16M-en | 16240509-1 | EN 61000-3-12 | EN 61000-3-11 | EMC TEST REPORT 1302895E Ed1 20013-08-14 | 1302895E Ed 1 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.1092 | 0.4842 | Equipment complying with IEC 61000-3-3 technical requirements
HP_1926 | Enertech | EcoAir | CTC EcoAir 406 1x230V | Heating only | Air Source | 1 | 230 |  |  |  |  | 10.3 | 2.369 | 10.3 | 2.369 | EcoAir 406 1x230V | Heat pump |  | 10.3 | 2.23 | 16220516-2-EU DoC CTC EcoAir 400-en | 16220516 | EN 61000-3-2 | EN 61000-3-3 | 21017-HF Enertech AB, EcoAir 406 1x230V | 21017-HF | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1927 | Enertech | EcoAir | CTC EcoAir 408 1x230V | Heating only | Air Source | 1 | 230 |  |  |  |  | 12.4 | 2.852 | 12.4 | 2.852 | EcoAir 408 1x230V | Heat pump |  | 12.4 | 2.73 | 16220516-2-EU DoC CTC EcoAir 400-en | 16220516 | EN 61000-3-2 | EN 61000-3-3 | 21018-HF Enertech AB, EcoAir 408 1x230V | 21018-HF | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No |  |  | No |  |  | No
HP_1928 | Enertech | EcoPart 425 | CTC EcoPart 425 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 21.1 | 14.6185 | 21.1 | 14.6185 | CTC EcoPart i425 | Heat pump |  | 21.1 | 10.8 | 16220521-2.1-EU DoC CTC EcoPart i425 i430 i435-en | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 20049-HF Harmonics and Flicker Enertech AB, EcoPart 425 | 20049-HF | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_1929 | Enertech | EcoPart 425 Pro | CTC EcoPart i425 Pro | Heating only | Ground Source | 3 | 400 |  |  |  |  | 22.2 | 15.3806 | 22.2 | 15.3806 | CTC EcoPart i425 | Heat pump |  | 22.2 | 15.4 | 16220521-2.1-EU DoC CTC EcoPart i425 i430 i435-en | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 20049-HF Harmonics and Flicker Enertech AB, EcoPart 425 | 20049-HF | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_1930 | Enertech | EcoPart 430 | CTC EcoPart 430 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 23.5 | 16.2813 | 23.5 | 16.2813 | CTC EcoPart 430 | Heat pump |  | 23.5 | 12.4 | 16220521-2.1-EU DoC CTC EcoPart i425 i430 i435-en | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 21007-HF Harmonics and Flicker Enertech AB, EcoPart 430 | 21007-HF | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.3068 | 0.522 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_1931 | Enertech | EcoPart 430 Pro | CTC EcoPart i430 Pro | Heating only | Ground Source | 3 | 400 |  |  |  |  | 24.6 | 17.0434 | 24.6 | 17.0434 | CTC EcoPart i430 Pro | Heat pump |  | 24.6 | 17 | 16220521-2.1-EU DoC CTC EcoPart i425 i430 i435-en | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 21007-HF Harmonics and Flicker Enertech AB, EcoPart 430 | 21007-HF | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.3068 | 0.522 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_1932 | Enertech | EcoPart 435 | CTC EcoPart 435 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 27.8 | 19.2604 | 27.8 | 19.2604 | CTC EcoPart i435 Pro | Heat pump |  | 27.8 | 14.8 | 16220521-2.1-EU DoC CTC EcoPart i425 i430 i435-en | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 21006-HF Harmonics and Flicker Enertech AB, EcoPart 435 | 21006-HF | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.3604 | 0.444 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_1933 | Enertech | EcoPart 435 Pro | CTC EcoPart i435 Pro | Heating only | Ground Source | 3 | 400 |  |  |  |  | 28.9 | 20.0225 | 28.9 | 20.0225 | CTC EcoPart i435 Pro | Heat pump |  | 28.9 | 19.4 | 16220521-2.1-EU DoC CTC EcoPart i425 i430 i435-en | 16220521 | EN 61000-3-12 | EN 61000-3-11 | 21006-HF Harmonics and Flicker Enertech AB, EcoPart 435 | 21006-HF | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.3604 | 0.444 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No |  | Yes | No |  | Yes | No
HP_1934 | Enertech | EcoAir | CTC EcoAir 410 1x230V | Heating only | Air Source | 1 | 230 |  |  |  |  | 18.8 | 4.324 | 18.8 | 4.324 | EcoAir 410 1x230V | Heat pump |  | 18.8 | 3.87 | 16250079-1-EU DoC CTC EcoAir 410 1x230V-en | 162500791 | EN 61000-3-12 | EN 61000-3-11 | 21019-HF Enertech AB, EcoAir 410 1x230V | 21019-HF | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.392
HP_2001 | Cool Energy | Eco Store | CE-ES200 | Heating only | Air Source | 1 | 230 |  |  |  |  | 2.726 | 0.627 | 6.639 | 1.527 | CE-ES200 | Whole system |  | 6.639 | 1.527 | DC_COOLENERGYrev2.pdf | DC_COOLENERGYrev2 | EN 61000-3-2 | EN 61000-3-3 | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | 18-HG-0267.E01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No
HP_2002 | Cool Energy | Eco Store | CE-ES200H-TMG | Heating only | Air Source | 1 | 230 |  |  |  |  | 2.726 | 0.627 | 6.639 | 1.527 | CE-ES200H-TMG | Whole system |  | 6.639 | 1.527 | DC_COOLENERGYrev2.pdf | DC_COOLENERGYrev2 | EN 61000-3-2 | EN 61000-3-3 | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | 18-HG-0267.E01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No
HP_2003 | Cool Energy | Eco Store | CE-ES300 | Heating only | Air Source | 1 | 230 |  |  |  |  | 2.726 | 0.627 | 6.639 | 1.527 | CE-ES300 | Whole system |  | 6.639 | 1.527 | DC_COOLENERGYrev2.pdf | DC_COOLENERGYrev2 | EN 61000-3-2 | EN 61000-3-3 | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | 18-HG-0267.E01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No
HP_2004 | Cool Energy | Eco Store | CE-ES300H-TMG | Heating only | Air Source | 1 | 230 |  |  |  |  | 2.726 | 0.627 | 6.639 | 1.527 | CE-ES300H-TMG | Whole system |  | 6.639 | 1.527 | DC_COOLENERGYrev2.pdf | DC_COOLENERGYrev2 | EN 61000-3-2 | EN 61000-3-3 | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | 18-HG-0267.E01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No | No
HP_2005 | Cool Energy | CE-iVT9 | CE-iVT9 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.8 | 3.4 | 14.8 | 3.4 | CE-iVT9 | Heat pump |  | 14.8 | 2.67 | ISETC.000120200914 CE.pdf | ISETC.000120200914 | EN 61000-3-2 | EN 61000-3-3 | EMC Report-CE-iVT9 | POCE201113041GRE | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No
HP_2006 | Cool Energy | CE-iVT26-3PH | CE-iVT26-3PH | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 12.1 | 8.38 | 12.1 | 8.38 | CE-iVT26-3PH | Heat pump |  | 12.1 | 8.38 | ISETC.000120200914 CE.pdf | ISETC.000120200914 | EN 61000-3-2 | EN 61000-3-3 | EMC Report-CE-iVT26-3PH | POCE201113039FRE | Yes | Yes | Yes | Yes | Yes | Yes | No | EMC Report-CE-iVT26-3PH | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No
HP_2007 | Cool Energy | CE-iVT18 | CE-iVT18 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | CE-iVT18 | Heat pump |  | 25 | 5.75 | UKCA IVT&ET.pdf | E8AUK 117104 0001 Rev. 00 | EN 61000-3-12 | EN 61000-3-11 | EMC Report IVT&ET & Harmonic data | 64.711.22.00335.01UK | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2008 | Cool Energy | CE-H6 | CE-H6 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11 | 2.53 | 11 | 2.53 | CE-H6 | Heat pump |  | 11 | 2.4 | POCE191019020MCS CE-H6 CE Cert.pdf | POCE191019020MCS | EN 61000-3-2 | EN 61000-3-3 | cool energy EMC Test report 200804148GZU-001 | 200804148GZU-001 | Yes | Yes | Yes | Yes | Yes | Yes | No | cool energy EMC Test report 200804148GZU-001 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2009 | Cool Energy | CE-H8 | CE-H8 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14 | 3.22 | 14 | 3.22 | CE-H8 | Heat pump |  | 14 | 3.2 | POCE191019020MCS CE-H6 CE Cert.pdf | POCE191019020MCS | EN 61000-3-2 | EN 61000-3-11 | cool energy EMC Test report 200804148GZU-001 | 200804148GZU-001 | Yes | No | No | No | Yes | No | Yes | cool energy EMC Test report 200804148GZU-001 | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.113
HP_2010 | Cool Energy | CE-H12 | CE-H12 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19 | 4.37 | 19 | 4.37 | CE-H12 | Heat pump |  | 19 | 4.4 | POCE191019020MCS CE-H6 CE Cert.pdf | POCE191019020MCS | EN 61000-3-12 | EN 61000-3-11 | cool energy EMC Test report 200804148GZU-001 | 200804148GZU-001 | Yes | No | No | No | Yes | No | Yes | cool energy EMC Test report 200804148GZU-001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_2011 | Cool Energy | CE-H17 | CE-H17 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | CE-H17 | Heat pump |  | 25 | 5.8 | CE-H17 CE-PH23 CE POCE191018024BCS COOL 空气能热泵.pdf | CE-H17 CE-PH23 CE POCE191018024BCS COOL 空气能热泵 | EN 61000-3-12 | EN 61000-3-11 | cool energy EMC Test report 200804148GZU-001 | 200804148GZU-001 | Yes | No | No | No | Yes | No | Yes | cool energy EMC Test report 200804148GZU-001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_2012 | Cool Energy | CE-PH7 | CE-PH7 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10 | 2.3 | 10 | 2.3 | CE-PH7 | Heat pump |  | 10 | 2.2 | POCE191019020MCS CE-H6 CE Cert.pdf | POCE191019020MCS | EN 61000-3-2 | EN 61000-3-3 | cool energy EMC Test report 200804148GZU-001 | 200804148GZU-001 | Yes | Yes | Yes | Yes | Yes | Yes | No | cool energy EMC Test report 200804148GZU-001 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2013 | Cool Energy | CE-PH14 | CE-PH14 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | CE-PH14 | Heat pump |  | 18 | 4.2 | POCE191019020MCS CE-H6 CE Cert.pdf | POCE191019020MCS | EN 61000-3-12 | EN 61000-3-11 | cool energy EMC Test report 200804148GZU-001 | 200804148GZU-001 | Yes | No | No | No | Yes | No | Yes | cool energy EMC Test report 200804148GZU-001 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.354
HP_2014 | Cool Energy | CE-iVT10-EVI | CE-iVT10-EVI | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.8 | 2.67 | 14.8 | 2.67 | CE-iVT10-EVI | Heat pump |  | 14.8 | 2.67 | CE-iVT9-CE-iVT10-EVI-CE-ET10-DOC.pdf | POCE201113038GCD | EN 61000-3-2 | EN 61000-3-3 | EMC Report-CE-iVT9 | POCE201113041GRE | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2015 | Cool Energy | CE-iVT22-EVI | CE-iVT22-EVI | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | CE-iVT22-EVI | Heat pump |  | 25 | 5.75 | UKCA IVT&ET.pdf | E8AUK 117104 0001 Rev. 00 | EN 61000-3-12 | EN 61000-3-11 | EMC Report IVT&ET & Harmonic data | 64.711.22.00335.01UK | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2016 | Cool Energy | CE-ET10 | CE-ET10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.8 | 2.67 | 14.8 | 2.67 | CE-ET10 | Heat pump |  | 14.8 | 2.67 | CE-iVT9-CE-iVT10-EVI-CE-ET10-DOC.pdf | POCE201113038GCD | EN 61000-3-2 | EN 61000-3-3 | EMC Report-CE-iVT9 | POCE201113041GRE | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2017 | Cool Energy | CE-ET15 | CE-ET15 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | CE-ET15 | Heat pump |  | 25 | 5.75 | UKCA IVT&ET.pdf | E8AUK 117104 0001 Rev. 00 | EN 61000-3-12 | EN 61000-3-11 | EMC Report IVT&ET & Harmonic data | 64.711.22.00335.01UK | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2018 | Cool Energy | CE-ET22 | CE-ET22 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | CE-ET22 | Heat pump |  | 25 | 5.75 | UKCA IVT&ET.pdf | E8AUK 117104 0001 Rev. 00 | EN 61000-3-12 | EN 61000-3-11 | EMC Report IVT&ET & Harmonic data | 64.711.22.00335.01UK | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2019 | Cool Energy | Eco Store | CE-ES200H-TMG | Heating only | Air Source | 1 | 230 |  |  |  |  | 2.726 | 0.627 | 6.639 | 1.527 | CE-ES200H-TMG | Whole system |  | 6.639 | 1.527 | DC_COOLENERGYrev2.pdf | DC_COOLENERGYrev2 | EN 61000-3-2 | EN 61000-3-3 | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | 18-HG-0267.E01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2020 | Cool Energy | Eco Store | CE-ES300H-TMG | Heating only | Air Source | 1 | 230 |  |  |  |  | 2.726 | 0.627 | 6.639 | 1.527 | CE-ES300H-TMG | Whole system |  | 6.639 | 1.527 | DC_COOLENERGYrev2.pdf | DC_COOLENERGYrev2 | EN 61000-3-2 | EN 61000-3-3 | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | 18-HG-0267.E01 | Yes | Yes | Yes | Yes | Yes | Yes | No | 18-HG-0267.E01 ECOSTORE CB EMV.pdf | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2101 | Heliotherm | Comfort Compact | S08L-M-CC | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19 | 4.37 | 19 | 4.37 | S08L-M-CC | Heat Pump |  | 19 | 4.4 | EC Declaration of Conformity CC | EC Declaration of Conformity CC | EN 61000-3-12 | EN 61000-3-11 | EMC_Test_Report_220V_H-Series | T8M21007-0198-E-16 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_2102 | Heliotherm | Comfort Compact | S12L-M-CC | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 7 | S12L-M-CC | Heat Pump |  | 25 | 5.75 | EC Declaration of Conformity CC | EC Declaration of Conformity CC | EN 61000-3-12 | EN 61000-3-11 | Intertek Test Report CC_BC | 2238586KAU-001 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_2103 | Heliotherm | Comfort Compact | S18L-M-CC | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 36 | 8.28 | 36 | 8.5 | S18L-M-CC | Heat Pump |  | 36 | 8.28 | EC Declaration of Conformity CC | EC Declaration of Conformity CC | EN 61000-3-12 | EN 61000-3-11 | Intertek Test Report CC_BC | 2238586KAU-001 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_2104 | Heliotherm | Comfort Compact | HP12S16W-M-BC | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 6.5 | HP12S16W-M-BC | Heat Pump |  | 25 | 5.75 | EG Konformitätserklärung_Sole_mod_BC | EC Declaration of Conformity BC BW | EN 61000-3-12 | EN 61000-3-11 | Intertek Test Report CC_BC | 2238586KAU-001 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_2105 | Heliotherm | Basic Comfort | HP20S25W-M-BC | Heating & Cooling | Ground Source | 1 | 230 |  |  |  |  | 36 | 8.28 | 36 | 8.5 | HP20S25W-M-BC | Heat Pump |  | 36 | 8.28 | EG Konformitätserklärung_Sole_mod_BC | EC Declaration of Conformity BC BW | EN 61000-3-12 | EN 61000-3-11 | Intertekt Test Report CC_BC | 2238586KAU-001 | Yes | Yes | Yes | Yes | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | No |  |  | No |  |  | No
HP_2201 | Oilon | Lämpöässä | ESi 11 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | ESi 11 1x230V | Whole system |  | 32 | 7.36 | Declaration of conformity_Esi.pdf | Declaration of conformity_Esi | EN 61000-3-12 | EN 61000-3-11 | 39-14720-1-emc.pdf | 39-14720-1/EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.2208 | 0.23958 | Requires Zsource ≤Zmax | 0.27 | Yes | No | - | Yes | No | - | Yes | No | -
HP_2202 | Oilon | Lämpöässä | Eli 60 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 32.3 | 22.38 | 32.3 | 22.38 | Eli 60 | Whole system |  | 32.3 | 22.4 | Declaration of conformity_ELi.pdf | Declaration of conformity_Eli | EN 61000-3-12 | EN 61000-3-11 | 39-14720-4-emc.pdf | 39-14720-4/EMC | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 16 | 0.69836 | 0.229 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No | - | Yes | No | - | Yes | No | -
HP_2203 | Oilon | Lämpöässä | Emi 43 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 50 | 34.64 | 50 | 34.64 | Emi 43 | Whole system |  | 50 | 34.64 | Declaration of conformity_Emi.pdf | Declaration of conformity_Emi | EN 61000-3-12 | EN 61000-3-11 | 39-14720-3-emc.pdf | 39-14720-3/EMC | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 22 | 0.762 | 0.21 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No | - | Yes | No | - | Yes | No | -
HP_2204 | Oilon | Lämpöässä | Vsi 8 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 7 | 4.85 | 7 | 4.85 | Vsi 8 | Whole system |  | 7 | 4.85 | Declaration of conformity_Vsi.pdf | Declaration of conformity_Vsi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ | 39-14811/1/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2205 | Oilon | Lämpöässä | Esi 6 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 7 | 4.85 | 7 | 4.85 | Esi 6 | Whole system |  | 7 | 4.85 | Declaration of conformity_Esi.pdf | Declaration of conformity_Esi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ | 39-14811/1/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2206 | Oilon | Lämpöässä | Vmi6 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 7 | 4.85 | 7 | 4.85 | Vmi6 | Whole system |  | 7 | 4.85 | Declaration of conformity_Vmi.pdf | Declaration of conformity_Vmi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ | 39-14811/1/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2207 | Oilon | Lämpöässä | Esi 11 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | Esi 11 | Whole system |  | 10 | 6.93 | Declaration of conformity_Esi.pdf | Declaration of conformity_Esi | EN 61000-3-2 | EN 61000-3-3 | 39-148811-EZ | 39-148811/2/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2208 | Oilon | Lämpöässä | Vmi 11 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | Vmi 11 | Whole system |  | 10 | 6.93 | Declaration of conformity_Vmi.pdf | Declaration of conformity_Vmi | EN 61000-3-2 | EN 61000-3-3 | 39-148811-EZ | 39-148811/2/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2209 | Oilon | Lämpöässä | Vsi 12 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 10 | 6.93 | 10 | 6.93 | Vsi 12 | Whole system |  | 10 | 6.93 | Declaration of conformity_Vsi.pdf | Declaration of conformity_Vsi | EN 61000-3-2 | EN 61000-3-3 | 39-148811-EZ | 39-148811/2/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2210 | Oilon | Lämpöässä | Esi 14 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 11 | 7.62 | 11 | 7.62 | Esi 14 | Whole system |  | 11 | 7.62 | Declaration of conformity_Esi.pdf | Declaration of conformity_Esi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ | 39-14811/3/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2211 | Oilon | Lämpöässä | Vmi 14 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 11 | 7.62 | 11 | 7.62 | Vmi 14 | Whole system |  | 11 | 7.62 | Declaration of conformity_Vmi.pdf | Declaration of conformity_Vmi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ | 39-14811/3/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2212 | Oilon | Lämpöässä | Vsi 14 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 11 | 7.62 | 11 | 7.62 | Vsi 14 | Whole system |  | 11 | 7.62 | Declaration of conformity_Vsi.pdf | Declaration of conformity_Vsi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ | 39-14811/3/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2213 | Oilon | Lämpöässä | Esi 14 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | Esi 14 1x230V | Whole system |  | 32 | 7.36 | Declaration of conformity_Esi.pdf | Declaration of conformity_Esi | EN 61000-3-12 | EN 61000-3-11 | 39-14811-EZ.pdf | 39-14811/4/EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 27 | 0.2484 | 0.21296 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2214 | Oilon | Lämpöässä | Vmi 14 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | Vmi 14 1x230V | Whole system |  | 32 | 7.36 | Declaration of conformity_Vmi.pdf | Declaration of conformity_Vmi | EN 61000-3-12 | EN 61000-3-11 | 39-14811-EZ.pdf | 39-14811/4/EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 27 | 0.2484 | 0.21296 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2215 | Oilon | Lämpöässä | Esi17 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | Esi17 | Whole system |  | 13 | 9.01 | Declaration of conformity_Esi.pdf | Declaration of conformity_Esi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ.pdf | 39-14811/5/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2216 | Oilon | Lämpöässä | Vmi 17 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 13 | 9.01 | 13 | 9.01 | Vmi 17 | Whole system |  | 13 | 9.01 | Declaration of conformity_Vmi.pdf | Declaration of conformity_Vmi | EN 61000-3-2 | EN 61000-3-3 | 39-14811-EZ.pdf | 39-14811/5/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2217 | Oilon | Lämpöässä | Emi 22 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 24 | 16.63 | 24 | 16.63 | Emi 22 | Whole system |  | 24 | 16.63 | Declaration of conformity_Emi.pdf | Declaration of conformity_Emi | EN 61000-3-12 | EN 61000-3-11 | 39-14811-EZ.pdf | 39-14811/6/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2218 | Oilon | Lämpöässä | Emi 28 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 28 | 19.4 | 28 | 19.4 | Emi 28 | Whole system |  | 28 | 19.4 | Declaration of conformity_Emi.pdf | Declaration of conformity_Emi | EN 61000-3-12 | EN 61000-3-11 | 39-14811-EZ.pdf | 39-14811/7/EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 21 | 0.364 | 0.44 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2219 | Oilon | Lämpöässä | Vmi 11 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | Vmi 11 | Whole system |  | 32 | 7.36 | Declaration of conformity_Vmi.pdf | Declaration of conformity_Vmi | EN 61000-3-12 | EN 61000-3-11 | 39-14720-1-emc.pdf | 39-14720-1/EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.2208 | 0.2395 | Requires Zsource ≤Zmax | 0.27 | Yes | No | - | Yes | No | - | Yes | No | -
HP_2220 | Oilon | Lämpöässä | VSi 12 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | VSi 12 1x230V | Whole system |  | 32 | 7.36 | Declaration of conformity_Vsi.pdf | Declaration of conformity_Vsi | EN 61000-3-12 | EN 61000-3-11 | 39-14720-1-emc.pdf | 39-14720-1/EMC | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 30 | 0.2208 | 0.23958 | Requires Zsource ≤Zmax | 0.27 | Yes | No | - | Yes | No | - | Yes | No | -
HP_2221 | Oilon | Lämpöässä | Vsi 6 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 7 | 4.85 | 7 | 4.85 | Vsi 6 | Whole system |  | 7 | 4.85 | Declaration of conformity_Vsi.pdf | Declaration of conformity_Vsi | EN 61000-3-2 | EN 61000-3-3 | 39-15062-1-emc.pdf | 39-15062/1/EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2222 | Oilon | Lämpöässä | Vsi 8 1x230V | Heating only | Ground Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | Vsi 8 1x230V | Whole system |  | 25 | 5.75 | Declaration of conformity_Vsi.pdf | Declaration of conformity_Vsi | EN 61000-3-12 | EN 61000-3-11 | 39-15062-2-EMC-příloha-1 EN corrected.pdf | 39-15062/2/EMC | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.183 | Yes | Yes | 10 | Yes | Yes | 10 | Yes | Yes | 10
HP_2301 | Global Energy Systems | Caernarfon | CAER410MOD1 | Heating only | Air Source | 1 | 230 |  |  |  |  | 34 | 7.82 | 34 | 7.82 | CAER410MOD1 | Heat pump | CAER410MOD1 | 34 | 8.2 | Caernafon Technical File - EC Declaration of Conformity | GES/TEC/06 | EN 61000-3-12 | EN 61000-3-11 | Caernarfon Flicker and Harmonics Test Report | GES-TST-001-05-05-20 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 14 | 0.10948 | 0.48319 | Requires Zsource ≤Zmax | 0.25 | Yes | No | - | Yes | No |  | No |  | -
HP_2302 | Global Energy Systems | Oxford | OXFR410MOD1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 17 | 3.91 | 17 | 3.91 | OXFR410MOD1 | Heat pump | OXFR410MOD1 | 17 | 3.91 | Oxford EMC Directive CE Declaration |  | EN 61000-3-12 | EN 61000-3-11 | GER21F180E | GER21F180E | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2303 | Global Energy Systems | Winchester | WINR410MOD1 | Heating only | Air Source | 3 | 400 |  |  |  |  | 12.1244 | 8.4 | 12.1244 | 8.4 | WINR410MOD1 | Heat pump | WINR410MOD1 | 12.12 | 8.4 | Winchester CE Declaration | GES/TEC/06 | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2401 | Viessmann | Vitocal 200-G | BWC-M 201.B06 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 52.2 | 12.01 | 52.2 | 12.01 | BWC-M 201.B06 | Heat pump |  | 13.1 | 2.71 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-12 | EN 61000-3-11 | 14e510-Viessmann-Balz-rp-emc.pdf | 14/510 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18
[17 empty] | Back-up heater - on-board |  | 39.1 | 9 |  |  | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2402 | Viessmann | Vitocal 200-G | BWC-M 201.B08 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 56.5 | 13 | 56.5 | 13 | BWC-M 201.B08 | Heat pump |  | 17.4 | 4 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-12 | EN 61000-3-11 | 14e510-Viessmann-Balz-rp-emc.pdf | 14/510 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18
[17 empty] | Back-up heater - on-board |  | 39.1 | 9 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2403 | Viessmann | Vitocal 200-G | BWC-M 201.B10 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 62.2 | 14.31 | 62.2 | 14.31 | BWC-M 201.B10 | Heat pump |  | 23.1 | 5.3 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-12 | EN 61000-3-11 | 14e510-Viessmann-Balz-rp-emc.pdf | 14/510 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.18
[17 empty] | Back-up heater - on-board |  | 39.1 | 9 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2404 | Viessmann | Vitocal 100-A | AWO-M-AC 101.A06 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.1 | 3.47 | 15.1 | 3.47 | AWO-M-AC 101.A06 | Heat pump |  | 15.1 | 3.47 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-2 | EN 61000-3-3 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No
HP_2405 | Viessmann | Vitocal 100-A | AWO-M-AC-AF 101.A06 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.6 | 3.59 | 15.6 | 3.59 | AWO-M-AC-AF 101.A06 | Heat pump |  | 15.6 | 3.59 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-2 | EN 61000-3-3 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No
HP_2406 | Viessmann | Vitocal 100-A | AWO-M-AC 101.A08 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 17 | 3.91 | 17 | 3.91 | AWO-M-AC 101.A08 | Heat pump |  | 17 | 3.91 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2407 | Viessmann | Vitocal 100-A | AWO-M-AC-AF 101.A08 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 17.6 | 4.05 | 17.6 | 4.05 | AWO-M-AC-AF 101.A08 | Heat pump |  | 17.6 | 4.05 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2408 | Viessmann | Vitocal 100-A | AWO-M-AC 101.A10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 20.2 | 4.65 | 20.2 | 4.65 | AWO-M-AC 101.A10 | Heat pump |  | 20.2 | 4.65 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2409 | Viessmann | Vitocal 100-A | AWO-M-AC-AF 101.A10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 20.7 | 4.76 | 20.7 | 4.76 | AWO-M-AC-AF 101.A10 | Heat pump |  | 20.7 | 4.76 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2410 | Viessmann | Vitocal 100-A | AWO-M-AC 101.A12 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 22.1 | 5.08 | 22.1 | 5.08 | AWO-M-AC 101.A12 | Heat pump |  | 22.1 | 5.08 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2411 | Viessmann | Vitocal 100-A | AWO-M-AC-AF 101.A12 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 22.7 | 5.22 | 22.7 | 5.22 | AWO-M-AC-AF 101.A12 | Heat pump |  | 22.7 | 5.22 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | COMPATIBILITA’ ELETTROMAGNETICA_.pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | CC2102B / Viessmann_Vitocal-100A_ENA declaration | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2412 | Viessmann | Vitocal 300-G | BWC 301.C06 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 22 | 15.24 | 22 | 15.24 | BWC 301.C06 | Heat pump |  | 9 | 6.24 | 4766784_VC300G BWC declaration of conformity_2020.pdf | 4766784 GB | EN 61000-3-2 | EN 61000-3-3 | 14e511-Viessmann-Balz-rp-emc.pdf | 14/511 | Yes | Yes | Yes | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No
[16 empty] | BWC 301.C06 | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2413 | Viessmann | Vitocal 300-G | BWC 301.C12 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 25 | 17.32 | 25 | 17.32 | BWC 301.C12 | Heat pump |  | 12 | 8.32 | 4766784_VC300G BWC declaration of conformity_2020.pdf | 4766784 GB | EN 61000-3-2 | EN 61000-3-3 | 14e511-Viessmann-Balz-rp-emc.pdf | 14/511 | Yes | Yes | Yes | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No
[16 empty] | BWC 301.C12 | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2414 | Viessmann | Vitocal 300-G | BWC 301.C16 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 25 | 17.32 | 25 | 17.32 | BWC 301.C16 | Heat pump |  | 12 | 8.32 | 4766784_VC300G BWC declaration of conformity_2020.pdf | 4766784 GB | EN 61000-3-2 | EN 61000-3-3 | 14e511-Viessmann-Balz-rp-emc.pdf | 14/511 | Yes | Yes | Yes | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes | No
[16 empty] | BWC 301.C16 | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2415 | Viessmann | Vitocal 100-A | AWO-M-AC-AF 101.A16 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 31 | 7.13 | 31 | 7.13 | AWO-M-AC-AF 101.A16 | Heat pump |  | 31 | 7.13 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | C19180301 i-32V516 (CMC_2).pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | C19180301 / Viessmann_Vitocal-100A_ENA declaration | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.171 | 0.3093 | Equipment complying with IEC 61000-3-3 technical requirements | [7 empty] | Yes | No
HP_2416 | Viessmann | Vitocal 100-A | AWO-M-AC 101.A14 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 28.6 | 6.58 | 28.6 | 6.58 | AWO-M-AC 101.A14 | Heat pump |  | 28.6 | 6.58 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | C19180301 i-32V516 (CMC_2).pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | C19180301 / Viessmann_Vitocal-100A_ENA declaration | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.171 | 0.3093 | Equipment complying with IEC 61000-3-3 technical requirements | [7 empty] | Yes | No
HP_2417 | Viessmann | Vitocal 100-A | AWO-M-AC-AF 101.A14 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 29.2 | 6.72 | 29.2 | 6.72 | AWO-M-AC-AF 101.A14 | Heat pump |  | 29.2 | 6.72 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | C19180301 i-32V516 (CMC_2).pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | C19180301 / Viessmann_Vitocal-100A_ENA declaration | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.171 | 0.3093 | Equipment complying with IEC 61000-3-3 technical requirements | [7 empty] | Yes | No
HP_2418 | Viessmann | Vitocal 100-A | AWO-M-AC 101.A16 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 30.4 | 6.99 | 30.4 | 6.99 | AWO-M-AC 101.A16 | Heat pump |  | 30.4 | 6.99 | 4762881_VC 100A_declaration of conformity.pdf | 4762881 GB 9/2019 | EN 61000-3-12 | EN 61000-3-11 | C19180301 i-32V516 (CMC_2).pdf & Viessmann_Vitocal-100A_ENA declaration.pdf | C19180301 / Viessmann_Vitocal-100A_ENA declaration | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 26 | 0.171 | 0.3093 | Equipment complying with IEC 61000-3-3 technical requirements | [7 empty] | Yes | No
HP_2419 | Viessmann | Vitocal 222-A | AWOT-M-E-AC 221.A10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 58.9 | 13.547 | 58.9 | 13.547 | AWOT-M-E-AC 221.A10 | Heat pump |  | 19.9 | 4.577 | 4764251VKE00001_1.pdf | 4764251 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4764251 |  | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2420 | Viessmann | Vitocal 222-A | AWOT-M-E-AC 221.A13 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 62.3 | 14.33 | 62.3 | 14.33 | AWOT-M-E-AC 221.A13 | Heat pump |  | 23.3 | 5.36 | 4764251VKE00001_1.pdf | 4764251 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4764251 |  | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2421 | Viessmann | Vitocal 222-A | AWOT-M-E-AC 221.A16 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 62.3 | 14.33 | 62.3 | 14.33 | AWOT-M-E-AC 221.A16 | Heat pump |  | 23.3 | 5.36 | 4764251VKE00001_1.pdf | 4764251 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4764251 |  | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2422 | Viessmann | Vitocal 200-A | AWO-M-E-AC 201.A10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 58.9 | 13.547 | 58.9 | 13.547 | AWO-M-E-AC 201.A10 | Heat pump |  | 19.9 | 4.577 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2423 | Viessmann | Vitocal 200-A | AWO-M-E-AC 201.A13 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 62.3 | 14.33 | 62.3 | 14.33 | AWO-M-E-AC 201.A13 | Heat pump |  | 23.3 | 5.36 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2424 | Viessmann | Vitocal 200-A | AWO-M-E-AC 201.A16 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 62.3 | 14.33 | 62.3 | 14.33 | AWO-M-E-AC 201.A16 | Heat pump |  | 23.3 | 5.36 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2425 | Viessmann | Vitocal 222-G | BWT-M 221.B06 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 52.2 | 12.01 | 52.2 | 12.01 | BWT-M 221.B06 | Heat pump |  | 13.1 | 3 | 4758944VKE00002_1_222G.pdf | 4758944 GB 9/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e531-Viessmann-Balz-rp-aa_222G.pdf | 14/531 | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[16 empty] | BWT-M 221.B06 | Back-up heater - on-board |  | 39.1 | 9 | 4758944VKE00002_1_222G.pdf | 4758944 GB 9/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2426 | Viessmann | Vitocal 222-G | BWT-M 221.B08 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 56.5 | 13 | 56.5 | 13 | BWT-M 221.B08 | Heat pump |  | 17.4 | 4 | 4758944VKE00002_1_222G.pdf | 4758944 GB 9/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e531-Viessmann-Balz-rp-aa_222G.pdf | 14/531 | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[16 empty] | BWT-M 221.B08 | Back-up heater - on-board |  | 39.1 | 9 | 4758944VKE00002_1_222G.pdf | 4758944 GB 9/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2427 | Viessmann | Vitocal 222-G | BWT-M 221.B10 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 62.2 | 14.31 | 62.2 | 14.31 | BWT-M 221.B10 | Heat pump |  | 23.1 | 5.3 | 4758944VKE00002_1_222G.pdf | 4758944 GB 9/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e531-Viessmann-Balz-rp-aa_222G.pdf | 14/531 | Yes | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[16 empty] | BWT-M 221.B10 | Back-up heater - on-board |  | 39.1 | 9 | 4758944VKE00002_1_222G.pdf | 4758944 GB 9/2020 | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2428 | Viessmann | Vitocal 200-A | AWO-M 201.A10 | Heating only | Air Source | 1 | 230 |  |  |  |  | 19.9 | 4.58 | 19.9 | 4.58 | AWO-M 201.A10 | Heat pump |  | 19.9 | 4.577 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2429 | Viessmann | Vitocal 200-A | AWO-M 201.A13 | Heating only | Air Source | 1 | 230 |  |  |  |  | 23.3 | 5.36 | 23.3 | 5.36 | AWO-M 201.A13 | Heat pump |  | 23.3 | 5.36 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2430 | Viessmann | Vitocal 200-A | AWO-M 201.A16 | Heating only | Air Source | 1 | 230 |  |  |  |  | 23.3 | 5.36 | 23.3 | 5.36 | AWO-M 201.A16 | Heat pump |  | 23.3 | 5.36 | 4764653_Vitocal 2xx_declaration sheet.pdf | 4764653 GB 1/2020 | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.087 | 0.6803 | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | No
HP_2431 | Viessmann | Vitocal 200-A | AWO-M 201.A04 | Heating only | Air Source | 1 | 230 |  |  |  |  | 13.3 | 3.06 | 13.3 | 3.06 | AWO-M 201.A04 | Heat pump |  | 13.3 | 3.06 | 4764279_declaration of conformity_2019_1.pdf | 4764279 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_1.pdf, 17063759OS_1.pdf | 17063759 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2432 | Viessmann | Vitocal 200-A | AWO-M-E-AC 201.A04 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 52.3 | 12.03 | 52.3 | 12.03 | AWO-M-E-AC 201.A04 | Heat pump |  | 13.3 | 3.06 | 4764279_declaration of conformity_2019_1.pdf | 4764279 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_1.pdf, 17063759OS_1.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764279_declaration of conformity_2019_1.pdf | 4764279 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2433 | Viessmann | Vitocal 222-A | AWOT-M-E-AC 221.A04 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 52 | 11.96 | 52 | 11.96 | AWOT-M-E-AC 221.A04 | Heat pump |  | 13 | 2.99 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_2.pdf, 17063759OS_2.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2434 | Viessmann | Vitocal 222-A | AWOT-M-E-AC 221.A06 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.6 | 12.33 | 53.6 | 12.33 | AWOT-M-E-AC 221.A06 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_2.pdf, 17063759OS_2.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2435 | Viessmann | Vitocal 222-A | AWOT-M-E-AC 221.A08 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.6 | 12.33 | 53.6 | 12.33 | AWOT-M-E-AC 221.A08 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_2.pdf, 17063759OS_2.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2436 | Viessmann | Vitocal 222-A | AWOT-M-E- 221.A10 | Heating only | Air Source | 1 | 230 |  |  |  |  | 58.9 | 13.55 | 58.9 | 13.55 | AWOT-M-E 221.A10 | Heat pump |  | 19.9 | 4.58 | 4764251VKE00001_1.pdf | 4764251 GB | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4764251 GB |  | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No | Yes |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2437 | Viessmann | Vitocal 222-A | AWOT-M-E- 221.A13 | Heating only | Air Source | 1 | 230 |  |  |  |  | 62.3 | 14.33 | 62.3 | 14.33 | AWOT-M-E 221.A13 | Heat pump |  | 23.3 | 5.36 | 4764251VKE00001_1.pdf | 4764251 GB | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4764251 GB |  | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No | Yes |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2438 | Viessmann | Vitocal 222-A | AWOT-M-E- 221.A16 | Heating only | Air Source | 1 | 230 |  |  |  |  | 62.3 | 14.33 | 62.3 | 14.33 | AWOT-M-E 221.A16 | Heat pump |  | 23.3 | 5.36 | 4764251VKE00001_1.pdf | 4764251 GB | EN 61000-3-12 | EN 61000-3-11 | 17- ry 22b 82-1.pdf | 14/517 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4764251 GB |  | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No | Yes |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2439 | Viessmann | Vitocal 200-A | AWO-M 201.A06 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.6 | 3.36 | 14.6 | 3.36 | AWO-M 201.A06 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_1.pdf, 17063759OS_1.pdf | 17063759 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2440 | Viessmann | Vitocal 200-A | AWO-M 201.A08 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.6 | 3.36 | 14.6 | 3.36 | AWO-M 201.A08 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_1.pdf, 17063759OS_1.pdf | 17063759 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2441 | Viessmann | Vitocal 200-A | AWO-M-E-AC 201.A06 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.6 | 12.33 | 53.6 | 12.33 | AWO-M-E-AC 201.A06 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_1.pdf, 17063759OS_1.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2442 | Viessmann | Vitocal 200-A | AWO-M-E-AC 201.A08 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 53.6 | 12.33 | 53.6 | 12.33 | AWO-M-E-AC 201.A08 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_1.pdf, 17063759OS_1.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2443 | Viessmann | Vitocal 222-A | AWOT-M-E 221.A04 | Heating only | Air Source | 1 | 230 |  |  |  |  | 52 | 11.96 | 52 | 11.96 | AWOT-M-E 221.A04 | Heat pump |  | 13 | 2.99 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_2.pdf,17063759OS_2.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2444 | Viessmann | Vitocal 222-A | AWOT-M-E 221.A06 | Heating only | Air Source | 1 | 230 |  |  |  |  | 53.6 | 12.33 | 53.6 | 12.33 | AWOT-M-E 221.A06 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_2.pdf, 17063759OS_2.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2445 | Viessmann | Vitocal 222-A | AWOT-M-E 221.A08 | Heating only | Air Source | 1 | 230 |  |  |  |  | 53.6 | 12.33 | 53.6 | 12.33 | AWOT-M-E 221.A08 | Heat pump |  | 14.6 | 3.36 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-2 | EN 61000-3-3 | 17063759fl_2.pdf, 17063759OS_2.pdf | 17063759 | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 39 | 8.97 | 4764251VKE00001_1.pdf | 4765251 GB | EN 61000-3-12 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2446 | Viessmann | Vitocal 200-G | BWC 201.B06 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 17.8 | 12.33 | 17.8 | 12.33 | BWC 201.B06 | Heat pump |  | 4.8 | 3.32 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-2 | EN 61000-3-11 | 14e520-1-Viessmann-Balz-Rev 1-rp.pdf | 14/520/-1 | Yes | No | No | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2447 | Viessmann | Vitocal 200-G | BWC 201.B08 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 19.2 | 13.3 | 19.2 | 13.3 | BWC 201.B08 | Heat pump |  | 6.2 | 4.3 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-2 | EN 61000-3-11 | 14e520-1-Viessmann-Balz-Rev 1-rp.pdf | 14/520/-1 | Yes | No | No | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2448 | Viessmann | Vitocal 200-G | BWC 201.B10 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 20.4 | 14.13 | 20.4 | 14.13 | BWC 201.B10 | Heat pump |  | 7.4 | 5.13 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-2 | EN 61000-3-11 | 14e520-1-Viessmann-Balz-Rev 1-rp.pdf | 14/520/-1 | Yes | No | No | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2449 | Viessmann | Vitocal 200-G | BWC 201.B13 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 22.7 | 15.73 | 22.7 | 15.73 | BWC 201.B13 | Heat pump |  | 9.7 | 6.72 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-2 | EN 61000-3-11 | 14e520-1-Viessmann-Balz-Rev 1-rp.pdf | 14/520/-1 | Yes | No | No | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2450 | Viessmann | Vitocal 200-G | BWC 201.B17 | Heating only | Ground Source | 3 | 400 |  |  |  |  | 26 | 18.01 | 26 | 18.01 | BWC 201.B17 | Heat pump |  | 13 | 9 | 4765690_declaration of conformity_VC200G_2020_1.pdf | 4765690 GB | EN 61000-3-2 | EN 61000-3-11 | 14e520-1-Viessmann-Balz-Rev 1-rp.pdf | 14/520/-1 | Yes | No | No | No | Yes | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.26
[17 empty] | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-11 | 14e532-Viessmann-Balz-rp-aa.pdf | 14/532 | Yes | No | No | No |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.31
HP_2451 | Viessmann | Vitocal 151-A | AWOT-M-E-AC-AF 151.A10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 44.57 | 10.25 | 44.57 | 10.25 | AWOT-M-AC-AF 151.A10 | Heat Pump |  | 22.83 | 5.25 | Vitocal150A_EUDoC_4773736 | 4773736 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_3_2022-03-21_ | 285125-TL7-3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWOT-M-E-AC 151.A10 | Supplementary (boost) heater - external |  | 21.74 | 5 | Vitocal150A_EUDoC_4773737 | 4773736 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_1_2021-10-04 | 285125-TL7-1 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.47
HP_2452 | Viessmann | Vitocal 151-A | AWOT-M-E-AC-AF 151.A13 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 46.74 | 10.75 | 46.74 | 10.75 | AWOT-M-AC-AF 151.A13 | Heat Pump |  | 25 | 5.75 | Vitocal150A_EUDoC_4773736 | 4773736 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_3_2022-03-21_ | 285125-TL7-3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWOT-M-E-AC 151.A13 | Supplementary (boost) heater - external |  | 21.74 | 5 | Vitocal150A_EUDoC_4773737 | 4773736 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_1_2021-10-04 | 285125-TL7-1 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.47
HP_2453 | Viessmann | Vitocal 151-A | AWOT-M-E-AC-AF 151.A13 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.83 | 10.25 | 47.83 | 10.25 | AWOT-M-AC-AF 151.A16 | Heat Pump |  | 26.09 | 6 | Vitocal150A_EUDoC_4773736 | 4773736 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_3_2022-03-21_ | 285125-TL7-3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWOT-M-E-AC 151.A16 | Supplementary (boost) heater - external |  | 21.74 | 5 | Vitocal150A_EUDoC_4773737 | 4773736 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_1_2021-10-04 | 285125-TL7-1 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.47
HP_2454 | Viessmann | Vitocal 150-A | AWO-M-E-AC-AF 151.A10 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 44.57 | 10.25 | 44.57 | 10.25 | AWO-M-AC-AF 151.A10 | Heat Pump |  | 22.83 | 5.25 | Vitocal150A_EUDoC_4773707 | 4773707 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_3_2022-03-21_ | 285125-TL7-3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWO-M-E-AC 151.A10 | Supplementary (boost) heater - external |  | 21.74 | 5 | Vitocal150A_EUDoC_4773707 | 4773707 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_1_2021-10-04 | 285125-TL7-1 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.47
HP_2455 | Viessmann | Vitocal 150-A | AWO-M-E-AC-AF 151.A13 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 46.74 | 10.75 | 46.74 | 10.75 | AWO-M-AC-AF 151.A13 | Heat Pump |  | 25 | 5.75 | Vitocal150A_EUDoC_4773707 | 4773707 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_3_2022-03-21_ | 285125-TL7-3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWO-M-E-AC 151.A13 | Supplementary (boost) heater - external |  | 21.74 | 5 | Vitocal150A_EUDoC_4773707 | 4773707 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_1_2021-10-04 | 285125-TL7-1 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.47
HP_2456 | Viessmann | Vitocal 150-A | AWO-M-E-AC-AF 151.A16 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 47.83 | 11 | 47.83 | 11 | AWO-M-AC-AF 151.A16 | Heat Pump |  | 26.09 | 6 | Vitocal150A_EUDoC_4773707 | 4773707 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_3_2022-03-21_ | 285125-TL7-3 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWO-M-E-AC 151.A16 | Supplementary (boost) heater - external |  | 21.74 | 5 | Vitocal150A_EUDoC_4773707 | 4773707 GB 12/2021 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_285125_TL7_1_2021-10-04 | 285125-TL7-1 | Yes | Yes | Yes | Yes |  | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.47
HP_2501 | Alpha Innotec | LWDV 91-1/3 + HDV 9-1/3 | 100699HDV901 | Heating only | Air Source | 1 | 230 |  |  |  |  | 42.09 | 9.68 | 42.09 | 9.68 | LWDV 91-1/3 | Heat pump |  | 16 | 3.68 | 818186c ait LWDV | 818186c ait LWDV | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_Wärmepumpe LWDV9 |  | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | HDV901 | Supplementary (boost) heater - on-board |  | 26.09 | 6.0007 |  |  | EN 61000-3-12 | EN 61000-3-11 | TKB_ENA_Flicker_Durchlauferhitzer |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.265
HP_2502 | Alpha Innotec | SWCV 62 H1 | 10071941 | Heating only | Ground Source | 1 | 230 |  |  |  |  | 38.09 | 8.76 | 38.09 | 8.76 | 10071941 | Heat pump |  | 12 | 2.76 | 818172g aitd Konformitätserklärung mehrsprachig SWC 2019 Kat1 | 818172g aitd Konformitätserklärung mehrsprachig SWC 2019 Kat1 | EN 61000-3-2 | EN 61000-3-3 | EMVP_SWCV_62H3_1 |  | Yes | Yes | Yes | No | No | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 26.09 | 6.0007 |  |  | EN 61000-3-12 | EN 61000-3-11 | TKB_ENA_Flicker_Durchlauferhitzer |  | Yes | No | No | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.265
HP_2503 | Alpha Innotec | Jersey 5-1 | 1007984101 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 41.09 | 9.45 | 41.09 | 9.45 | 10079801 | Heat pump |  | 15 | 3.45 | 818207 Alpha-Innotec Jersey 5 and 7-1 | 818207 Alpha-Innotec Jersey 5 and 7-1 | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_5kW_2 |  | Yes | Yes | Yes | No | Yes | No | Yes | EMVP_AIT_Jersey 5-1 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | 15215041 | Supplementary (boost) heater - on-board |  | 26.09 | 6.0007 | 818207 Alpha-Innotec Jersey 5 and 7-1 | 818207 Alpha-Innotec Jersey 5 and 7-1 | EN 61000-3-12 | EN 61000-3-11 | EMVP_AIT_6kW Immersion Heater |  | Yes | No | No |  |  |  |  | EMVP_AIT_6kW Immersion Heater | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.265
HP_2504 | Alpha Innotec | LWD 50ASX+HMD1SE 2kW | 100603HMD02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22.7 | 5.22 | 22.7 | 5.22 | 10060301 | Heat pump |  | 14 | 3.22 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_LWD50 ASX_1 | EMVP_AIT_LWD50 ASX_1 | Yes | Yes | Yes | Yes | Yes | Yes | No | EMVP_AIT_LWD50 ASX_1 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | 15070841 | Supplementary (boost) heater - on-board |  | 8.7 | 2 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2505 | Alpha Innotec | LWD 50ASX+HMD1SE 4kW | 100603HMD02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 31.39 | 7.22 | 31.39 | 7.22 | 10060301 | Heat pump |  | 14 | 3.22 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_LWD50 ASX_1 | EMVP_AIT_LWD50 ASX_1 | Yes | Yes | Yes | No | Yes | No | Yes | EMVP_AIT_LWD50 ASX_1 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | 15070841 | Supplementary (boost) heater - on-board |  | 17.39 | 4 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.369
HP_2506 | Alpha Innotec | LWD 50ASX+HMD1SE 6kW | 100603HMD02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 40.09 | 9.22 | 40.09 | 9.22 | 10060301 | Heat pump |  | 14 | 3.22 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_LWD50 ASX_1 | EMVP_AIT_LWD50 ASX_1 | Yes | Yes | Yes | No | Yes | No | Yes | EMVP_AIT_LWD50 ASX_1 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | 15070841 | Supplementary (boost) heater - on-board |  | 26.09 | 6.0007 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-12 | EN 61000-3-11 | EMVP_AIT_6kW Immersion Heater | EMVP_AIT_6kW Immersion Heater | Yes | No | No |  |  |  |  | EMVP_AIT_6kW Immersion Heater | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.265
HP_2507 | Alpha Innotec | LWD 70ASX+HMD1SE 2kW | 100604HMD02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.6 | 5.66 | 24.6 | 5.66 | 10060401 | Heat pump |  | 15.9 | 3.22 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_7kW_3 | EMVP_AIT_7kW_1 | Yes | Yes | Yes | Yes | Yes | Yes | No | EMVP_AIT_7kW_3 | Not applicable |  |  | N/A | N/A | N/A
[16 empty] | 15070841 | Supplementary (boost) heater - on-board |  | 8.7 | 2 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A
HP_2508 | Alpha Innotec | LWD 70ASX+HMD1SE 4kW | 100604HMD02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 33.29 | 7.22 | 33.29 | 7.22 | 10060401 | Heat pump |  | 15.9 | 3.22 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_7kW_3 | EMVP_AIT_7kW_1 | Yes | Yes | Yes | Yes | No | No | Yes | EMVP_AIT_7kW_3 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | 15070841 | Supplementary (boost) heater - on-board |  | 17.39 | 4 |  |  | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | No | No | No |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.369
HP_2509 | Alpha Innotec | LWD 70ASX+HMD1SE 6kW | 100604HMD02 | Heating only | Air Source | 1 | 230 |  |  |  |  | 41.99 | 9.22 | 41.99 | 9.22 | 10060401 | Heat pump |  | 15.9 | 3.22 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-2 | EN 61000-3-3 | EMVP_AIT_7kW_3 | EMVP_AIT_7kW_1 | Yes | Yes | Yes | Yes | No | No | Yes | EMVP_AIT_7kW_3 | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | 15070841 | Supplementary (boost) heater - on-board |  | 26.09 | 6 | 818191c aitd Konformitätserklärung LWD HMD1 2022 | UK818191c | EN 61000-3-12 | EN 61000-3-11 | EMVP_AIT_6kW Immersion Heater | EMVP_AIT_6kW Immersion Heater | Yes | No | No | No |  |  |  | EMVP_AIT_6kW Immersion Heater | Not applicable |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.265
HP_2601 | Midea | MHC-V16W/D2RN8-B | MHC-V16W/D2RN8-B | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.95 | 6.2 | 8.95 | 6.2 | MHC-V16W/D2RN8-B | Heat pump |  | 8.95 | 6.2 | CE certificate & Reports12-16kW 3p64.711.18.05282.04-CERT EMC.pdf | E8A 072433 0915 Rev 03 | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2602 | Midea | MHC-V14W/D2RN8-B | MHC-V14W/D2RN8-B | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.37 | 5.8 | 8.37 | 5.8 | MHC-V14W/D2RN8-B | Heat pump |  | 8.37 | 5.8 | CE certificate & Reports12-16kW 3p64.711.18.05282.04-CERT EMC.pdf | E8A 072433 0915 Rev 03 | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2603 | Midea | MHC-V12W/D2RN8-B | MHC-V12W/D2RN8-B | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 7.94 | 5.5 | 7.94 | 5.5 | MHC-V12W/D2RN8-B | Heat pump |  | 7.94 | 5.5 | CE certificate & Reports12-16kW 3p64.711.18.05282.04-CERT EMC.pdf | E8A 072433 0915 Rev 03 | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2604 | Midea | MHC-V16W/D2N8-B | V16W/D2N8-B | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 26.96 | 6.2 | 26.96 | 6.2 | V16W/D2N8-B | Heat pump |  | 26.96 | 6.2 | 64.711.18.05280.04 CERT_EMC R32 Monobloc 单相单风轮机型 | E8A 072433 0913 Rev 03 | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2605 | Midea | MHC-V14W/D2N8-B | V14W/D2N8-B | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25.22 | 5.8 | 25.22 | 5.8 | V14W/D2N8-B | Heat pump |  | 25.22 | 5.8 | 64.711.18.05280.04 CERT_EMC R32 Monobloc 单相单风轮机型 | E8A 072433 0913 Rev 03 | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2606 | Midea | MHC-V12W/D2N8-B | V12W/D2N8-B | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.2 | 5.566 | 24.2 | 5.566 | V12W/D2N8-B | Heat pump |  | 24.2 | 5.5 | 64.711.18.05280.04 CERT_EMC R32 Monobloc 单相单风轮机型 |  | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2607 | Midea | MHC-V10W/D2N8-B | V10W/D2N8-B | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.2 | 3.726 | 16.2 | 3.726 | V10W/D2N8-B | Heat pump |  | 16.2 | 3.726 | CE Declaration of ConformityCE Declaration of Conformity - 4th gen. Monobloc |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V8W$D2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2608 | Midea | MHC-V8W/D2N8-B | V8W/D2N8-B | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.9 | 3.427 | 14.9 | 3.427 | V8W/D2N8-B | Heat pump |  | 14.9 | 3.427 | CE Declaration of ConformityCE Declaration of Conformity - 4th gen. Monobloc |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V8W$D2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2609 | Midea | MHC-V6W/D2N8-B | V6W/D2N8-B | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.9 | 2.7 | 11.9 | 2.7 | V6W/D2N8-B | Heat pump |  | 11.9 | 2.7 | CE Declaration of ConformityCE Declaration of Conformity - 4th gen. Monobloc |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V6W$D2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2610 | Midea | MHC-V4W/D2N8-B | V4W/D2N8-B | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.1 | 2.3 | 10.1 | 2.3 | V4W/D2N8-B | Heat pump |  | 10.1 | 2.3 | CE Declaration of ConformityCE Declaration of Conformity - 4th gen. Monobloc |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V6W$D2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2701 | Thermia | Mega XL - see WPE-I 88 H 400 Premium | Mega XL | Heating only | Ground Source | 3 | 400 |  |  |  |  | 54.2 | 37.55 | 54.2 | 37.55 | WPE-I 87 H 400 Premium | Heat pump | 4017212014158 | 54.2 | 37.55 | D0000086451-a.pdf | AO857/07.2018 | EN 61000-3-12 | EN 61000-3-11 | 1511389STO-001, Ed2.pdf | 1511389STO-001, Ed. 2 | No | No | No | No | No | No | Yes | 1511389STO-001, Ed. 2 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4150 |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.36
HP_2702 | Thermia | Mega M - see WPE-I 88 H 400 Premium | Mega M | Heating only | Ground Source | 3 | 400 |  |  |  |  | 26.38 | 18.28 | 26.38 | 18.28 | WPE-I 44 H 400 Premium | Heat pump | 4017212014134 | 26.38 | 18.2 | D0000086451-a.pdf | A0857/07.2018 | EN 61000-3-12 | EN 61000-3-11 | Harmonics Flicker Rise 7P06990 2018-01-22 | 7P06990 | No | No | No | No | Yes | No | Yes | 7P06990 | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 2193 |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.212
HP_2701 | Ideal | Alféa Extensa | Extensa A.I. 5 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | AH700227 | Heat pump | AH526349 | 13 | 2.99 | DoC UE Ideal Extensa AI 5-6 R32 20210715 |  | EN 61000-3-2 | EN 61000-3-3 | FG19-083CEN_Higher harmonic wave_ATW | FG19-083CEN-2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2702 | Ideal | Alféa Extensa | Extensa A.I. 6 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | AH700227 | Heat pump | AH526346 | 13 | 2.99 | DoC UE Ideal Extensa AI 5-6 R32 20210715 |  | EN 61000-3-2 | EN 61000-3-3 | FG19-083CEN_Higher harmonic wave_ATW | FG19-083CEN-2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2703 | Ideal | Alféa Extensa A.I. 8 R32 | Extensa A.I. 8 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | AH700228 | Heat pump | AH526347 | 18 | 4.14 | DoC UE Ideal Extensa AI 8-10 R32 20210728 |  | EN 61000-3-12 | EN 61000-3-3 | FG19-083CEN_Higher harmonic wave_ATW | FG19-083CEN-2 | Yes | Yes | Yes | Yes | Yes | Yes | No | SIC Letter HP R32 conformity to EMC Directive - ML 20210728 Ideal | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2704 | Ideal | Alféa Extensa A.I. 10 R32 | Extensa A.I. 10 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 19 | 4.37 | 19 | 4.37 | AH700229 | Heat pump | AH526348 | 19 | 4.37 | DoC UE Ideal Extensa AI 8-10 R32 20210728 |  | EN 61000-3-2 | EN 61000-3-3 | FG20-069CEN_Higher harmonic wave_ATW | FG20-069CEN | Yes | Yes | Yes | Yes | Yes | Yes | No | SIC Letter HP R32 conformity to EMC Directive - ML 20210728 Ideal | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_2705 | Ideal | Alféa Excellia A.I. TRI 16 | AH526244 | Heating only | Air Source | 3 | 400 |  |  |  |  | 10.5 | 7.2746 | 10.5 | 7.2746 | AH700178 | Whole system | AH526244 | 10.5 | 7.27 | declaration conformite UE_IDEAL Excellia AI 20190325 | 20190325 | EN 61000-3-2 | EN 61000-3-3 | FG11-141CEN・高調波・WSYK160DC9 WOYK160LCT | FG11-141CEN | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2706 | Ideal | Alféa Excellia A.I. 11 (without back-up) | AH526245 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | AH526245 | Whole system | AH526245 | 22 | 5.06 | DoC IDEAL Alfea Excellia AI 11 14 TRI 14 20210607.pdf | DoC UE Ideal Excellia AI 11 14 Tri 16 20210906 | EN 61000-3-12 | EN 61000-3-11 | FG11-140CEN・高調波・WSYG140DC6 WOYG140LCT.pdf | FG11-140CEN | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.09936 | 0.53241 | Requires Zsource ≤Zmax | 0.414
HP_2707 | Ideal | Alféa Excellia A.I. 14 (without back-up) | AH526243 | Heating only | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | AH526243 | Whole system | AH526243 | 25 | 5.75 | DoC IDEAL Alfea Excellia AI 11 14 TRI 14 20210607.pdf | DoC UE Ideal Excellia AI 11 14 Tri 16 20210906 | EN 61000-3-12 | EN 61000-3-11 | FG11-140CEN・高調波・WSYG140DC6 WOYG140LCT.pdf | FG11-140CEN | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.09936 | 0.53241 | Requires Zsource ≤Zmax | 0.414
HP_2708 | Ideal | Alféa Extensa | Extensa A.I. 5 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | AH700227 | Heat pump | AH526349 | 13 | 2.99 | DoC UE Ideal Extensa AI 5-6 R32 20210715 |  | EN 61000-3-2 | EN 61000-3-3 | FG19-083CEN_Higher harmonic wave_ATW | FG19-083CEN-2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2709 | Ideal | Alféa Extensa | Extensa A.I. 6 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | AH700227 | Heat pump | AH526346 | 13 | 2.99 | DoC UE Ideal Extensa AI 5-6 R32 20210715 |  | EN 61000-3-2 | EN 61000-3-3 | FG19-083CEN_Higher harmonic wave_ATW | FG19-083CEN-2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2710 | Ideal | Alféa Extensa A.I. 8 R32 | Extensa A.I. 8 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 18 | 4.14 | 18 | 4.14 | AH700228 | Heat pump | AH526347 | 18 | 4.14 | DoC UE Ideal Extensa AI 8-10 R32 20210728 |  | EN 61000-3-12 | EN 61000-3-3 | FG19-083CEN_Higher harmonic wave_ATW | FG19-083CEN-2 | Yes | Yes | Yes | Yes | Yes | Yes | No | SIC Letter HP R32 conformity to EMC Directive - ML 20210728 Ideal | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2711 | Ideal | Alféa Extensa A.I. 10 R32 | Extensa A.I. 10 R32 | Heating only | Air Source | 1 | 230 |  |  |  |  | 19 | 4.37 | 19 | 4.37 | AH700229 | Heat pump | AH526348 | 19 | 4.37 | DoC UE Ideal Extensa AI 8-10 R32 20210728 |  | EN 61000-3-2 | EN 61000-3-3 | FG20-069CEN_Higher harmonic wave_ATW | FG20-069CEN | Yes | Yes | Yes | Yes | Yes | Yes | No | SIC Letter HP R32 conformity to EMC Directive - ML 20210728 Ideal | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2712 | Ideal | Alféa Excellia A.I. TRI 16 | AH526244 | Heating only | Air Source | 3 | 400 |  |  |  |  | 10.5 | 7.27 | 10.5 | 7.27 | AH700178 | Heat pump | AH526244 | 13 | 2.99 | declaration conformite UE_IDEAL Excellia AI 20190325 | 20190325 | EN 61000-3-2 | EN 61000-3-3 | FG11-141CEN・高調波・WSYK160DC9 WOYK160LCT | FG11-141CEN | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2713 | Ideal | Alféa Excellia A.I. 11 | AH526245 | Heating only | Air Source | 1 | 230 |  |  |  |  | 22 | 5.06 | 22 | 5.06 | AH526245 | Heat pump | AH526245 | 22 | 5.06 | DoC IDEAL Alfea Excellia AI 11 14 TRI 14 20210607.pdf | DoC UE Ideal Excellia AI 11 14 Tri 16 20210906 | EN 61000-3-12 | EN 61000-3-11 | FG11-140CEN・高調波・WSYG140DC6 WOYG140LCT.pdf | FG11-140CEN | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.09936 | 0.53241 | Requires Zsource ≤Zmax | 0.414
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2714 | Ideal | Alféa Excellia A.I. 14 | AH526243 | Heating only | Air Source | 1 | 230 |  |  |  |  | 25 | 5.75 | 25 | 5.75 | AH526243 | Heat pump | AH526243 | 25 | 5.75 | DoC IDEAL Alfea Excellia AI 11 14 TRI 14 20210607.pdf | DoC UE Ideal Excellia AI 11 14 Tri 16 20210906 | EN 61000-3-12 | EN 61000-3-11 | FG11-140CEN・高調波・WSYG140DC6 WOYG140LCT.pdf | FG11-140CEN | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.09936 | 0.53241 | Requires Zsource ≤Zmax | 0.414
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_2901 | Renewable Energy Devices Ltd | A10-UHE | A10-UHE | Heating only | Air Source | 1 | 230 |  |  |  |  | 20 | 4.6 | 20 | 4.6 | A10-UHE | Heat pump | A10-UHE | 20 | 4.65 | RDC 010 declaration of conformity RED ASHP_10 &16kW | RDC010 | EN 61000-3-12 | EN 61000-3-11 | 21E9575-HF-1 Red Heat Pump.pdf | 21E9575-HF-1 | Yes | Yes | Yes | Yes | Yes | Yes | No | RED Product Specification_ENA | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No | No |  | No | No |  | No | No
HP_2902 | Renewable Energy Devices Ltd | A16-UHE | A16-UHE | Heating only | Air Source | 1 | 230 |  |  |  |  | 32 | 7.36 | 32 | 7.36 | A16-UHE | Heat pump | A16-UHE | 32 | 7.4 | RDC 010 declaration of conformity RED ASHP_10 &16kW | RDC010 | EN 61000-3-12 | EN 61000-3-11 | 21E9575-HF-1 Red Heat Pump.pdf | 21E9575-HF-1 | Yes | Yes | Yes | Yes | Yes | Yes | No | RED Product Specification_ENA | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | No | No |  | No | No |  | No | No
HP_3001 | Baxi | Assure | Mono 5 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.1 | 3.243 | 14.1 | 3.243 | Assure Mono 5 | Heat pump | 7754877 | 14.1 | 3.2 | Baxi Assure Mono DoC 5, 7 & 9kW.pdf | Ref: 501-3 | EN 61000-3-2 | EN 61000-3-3 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3002 | Baxi | Assure | Mono 7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.1 | 3.243 | 14.1 | 3.243 | Assure Mono 7 | Heat pump | 7754878 | 14.1 | 3.2 | Baxi Assure Mono DoC 5, 7 & 9kW.pdf | Ref: 501-3 | EN 61000-3-2 | EN 61000-3-3 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3003 | Baxi | Assure | Mono 9 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.1 | 3.243 | 14.1 | 3.243 | Assure Mono 9 | Heat pump | 7754879 | 14.1 | 3.2 | Baxi Assure Mono DoC 5, 7 & 9kW.pdf | Ref: 501-3 | EN 61000-3-2 | EN 61000-3-3 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3004 | Baxi | Assure | Mono 12 | Heating only | Air Source | 1 | 230 |  |  |  |  | 26.8 | 6.164 | 26.8 | 6.164 | Assure Mono 12 | Heat pump | 7754887 | 26.8 | 6.1 | Baxi Assure Monobloc DoC 12_16kW.pdf | Ref: 500-2 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3005 | Baxi | Assure | Mono 16 | Heating only | Air Source | 1 | 230 |  |  |  |  | 26.8 | 6.164 | 26.8 | 6.164 | Assure Mono 16 | Heat pump | 7754880 | 26.8 | 6.1 | Baxi Assure Monobloc DoC 12_16kW.pdf | Ref: 500-2 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3006 | Baxi | Remeha | 44 Ace B | Heating only | Air Source | 3 | 400 |  |  |  |  | 26.7 | 18.5 | 26.7 | 18.5 | E-HP-AW 44 Ace B | Heat pump |  | 26.7 | 18.5 | Remeha E-HP AW DoC UKCA 44, 88 & 168kW.pdf | Ref: 510-2 | EN 61000-3-12 | EN 61000-3-11 | 44_P20-Z-00474-002_en_Fin | P20-Z-00474-002 | Yes | No | No | No | Yes | No | Yes | Remeha E-HP-AW Installation & User Instructions | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.334
HP_3007 | Baxi | Assure | Mono 5 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.1 | 3.243 | 14.1 | 3.243 | Assure Mono 5 | Heat pump | 7754877 | 14.1 | 3.2 | Baxi Assure Mono DoC 5, 7 & 9kW.pdf | Ref: 501-3 | EN 61000-3-2 | EN 61000-3-3 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3008 | Baxi | Assure | Mono 7 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.1 | 3.243 | 14.1 | 3.243 | Assure Mono 7 | Heat pump | 7754878 | 14.1 | 3.2 | Baxi Assure Mono DoC 5, 7 & 9kW.pdf | Ref: 501-3 | EN 61000-3-2 | EN 61000-3-3 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3009 | Baxi | Assure | Mono 9 | Heating only | Air Source | 1 | 230 |  |  |  |  | 14.1 | 3.243 | 14.1 | 3.243 | Assure Mono 9 | Heat pump | 7754879 | 14.1 | 3.2 | Baxi Assure Mono DoC 5, 7 & 9kW.pdf | Ref: 501-3 | EN 61000-3-2 | EN 61000-3-3 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3010 | Baxi | Assure | Mono 12 | Heating only | Air Source | 1 | 230 |  |  |  |  | 26.8 | 6.164 | 26.8 | 6.164 | Assure Mono 12 | Heat pump | 7754887 | 26.8 | 6.1 | Baxi Assure Monobloc DoC 12_16kW.pdf | Ref: 500-2 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3011 | Baxi | Assure | Mono 16 | Heating only | Air Source | 1 | 230 |  |  |  |  | 26.8 | 6.164 | 26.8 | 6.164 | Assure Mono 16 | Heat pump | 7754880 | 26.8 | 6.1 | Baxi Assure Monobloc DoC 12_16kW.pdf | Ref: 500-2 | EN 61000-3-12 | EN 61000-3-11 | EMC Test Report on Monobloc Midea Heat Pump.pdf | 64.711.18.05280.01 | Yes | Yes | Yes | Yes | Yes | Yes | No | Baxi Assure Mono Installation Instructions | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3012 | Baxi | Remeha | 44 Ace B | Heating only | Air Source | 3 | 400 |  |  |  |  | 26.7 | 18.5 | 26.7 | 18.5 | E-HP-AW 44 Ace B | Heat pump |  | 26.7 | 18.5 | Remeha E-HP AW DoC UKCA 44, 88 & 168kW.pdf | Ref: 510-2 | EN 61000-3-12 | EN 61000-3-11 | 44_P20-Z-00474-002_en_Fin | P20-Z-00474-002 | Yes | No | No | No | Yes | Yes | No | Remeha E-HP-AW Installation & User Instructions | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Zsource ≤Zmax | 0.334
[17 empty] | Supplementary (boost) heater - external (see Note 1 below) |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3101 | OCHSNER Wärmepumpen | AIR 41 C12A | 287060 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.8 | 17.1819 | 24.8 | 17.1819 |  | Heat pump |  | 24.8 | 17.2 | CE-AIR M4 (AIR 29 C12A _ AIR 41 C12A)-ML01.pdf | 982058-CE-AIR M4 (AIR 29 C12A / AIR 41 C12A)-ML01 | EN 61000-3-12 | EN 61000-3-11 | 20-218E gesamt_signed_2x & EMV-test report_AIR 41_2021 | FM-INE-EMV-EMC-0100a_en & 39-15286/1/EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.3055 | 0.524 | Equipment complying with IEC 61000-3-3 technical requirements
HP_3102 | OCHSNER Wärmepumpen | AIR 41 C12A | 287060 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 24.8 | 17.1819 | 24.8 | 17.1819 |  | Heat pump |  | 24.8 | 17.2 | CE-AIR M4 (AIR 29 C12A _ AIR 41 C12A)-ML01.pdf | 982058-CE-AIR M4 (AIR 29 C12A / AIR 41 C12A)-ML01 | EN 61000-3-12 | EN 61000-3-11 | 20-218E gesamt_signed_2x & EMV-test report_AIR 41_2021 | FM-INE-EMV-EMC-0100a_en & 39-15286/1/EMC | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 18 | 0.3055 | 0.524 | Equipment complying with IEC 61000-3-3 technical requirements
[17 empty] | Supplementary (boost) heater - external |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3201 | Nilan | Compact P | Compact P | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 9.6 | 2.208 | 9.6 | 2.208 | Compact P | Heat pump |  | 9.6 | 2.208 | Compact-P_declaration-of-conformity .pdf |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable |  | Yes |  |  | Yes |  |  | Yes
HP_3301 | Toshiba | R32 ESTIA Series 1 | HWT-401HW-E + HWT-601XWHM3W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.6 | 6.35 | 27.6 | 6.35 | HWT-401HW-E | Heat pump |  | 14.6 | 3.36 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | HWT-601XWHM3W-E | Back-up heater - on-board |  | 13 | 3 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3302 | Toshiba | R32 ESTIA Series 1 | HWT-401HW-E + HWT-601XWHT6W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13.53 | 9.36 | 27.6 | 9.36 | HWT-401HW-E | Heat pump |  | 14.6 | 3.36 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [8 empty] | HWT-601XWHT6W-E | Back-up heater - on-board |  | 13 | 6 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3303 | Toshiba | R32 ESTIA Series 1 | HWT-601HW-E + HWT-601XWHM3W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.6 | 6.36 | 27.6 | 6.36 | HWT-601HW-E | Heat pump |  | 14.6 | 3.36 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | HWT-601XWHM3W-E | Back-up heater - on-board |  | 13 | 3 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3304 | Toshiba | R32 ESTIA Series 1 | HWT-601HW-E + HWT-601XWHT6W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 13.53 | 9.36 | 27.6 | 9.36 | HWT-601HW-E | Heat pump |  | 14.6 | 3.36 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [8 empty] | HWT-601XWHT6W-E | Back-up heater - on-board |  | 13 | 6 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3305 | Toshiba | R32 ESTIA Series 1 | HWT-801HW-E + HWT-1101XWHM3W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 33.3 | 7.66 | 33.3 | 7.66 | HWT-801HW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWT-1101XWHM3W-E | Back-up heater - on-board |  | 13 | 3 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3306 | Toshiba | R32 ESTIA Series 1 | HWT-801HW-E + HWT-1101XWHT6W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.43 | 10.67 | 33.3 | 10.67 | HWT-801HW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT6W-E | Back-up heater - on-board |  | 13 | 6 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3307 | Toshiba | R32 ESTIA Series 1 | HWT-801HW-E + HWT-1101XWHT9W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.77 | 13.67 | 33.3 | 13.67 | HWT-801HW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT9W-E | Back-up heater - on-board |  | 13 | 9 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3308 | Toshiba | R32 ESTIA Series 1 | HWT-1101HW-E + HWT-1101XWHM3W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 33.3 | 7.66 | 33.3 | 7.66 | HWT-1101HW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWT-1101XWHM3W-E | Back-up heater - on-board |  | 13 | 3 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3309 | Toshiba | R32 ESTIA Series 1 | HWT-1101HW-E + HWT-1101XWHT6W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.43 | 10.67 | 33.3 | 10.67 | HWT-1101HW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT6W-E | Back-up heater - on-board |  | 13 | 6 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3310 | Toshiba | R32 ESTIA Series 1 | HWT-1101HW-E + HWT-1101XWHT9W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.77 | 13.67 | 33.3 | 13.67 | HWT-1101HW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT9W-E | Back-up heater - on-board |  | 13 | 9 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3311 | Toshiba | R32 ESTIA Series 1 | HWT-801HRW-E + HWT-1101XWHM3W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 33.3 | 7.66 | 33.3 | 7.66 | HWT-801HRW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWT-1101XWHM3W-E | Back-up heater - on-board |  | 13 | 3 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3312 | Toshiba | R32 ESTIA Series 1 | HWT-801HRW-E + HWT-1101XWHT6W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.43 | 10.67 | 33.3 | 10.67 | HWT-801HRW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT6W-E | Back-up heater - on-board |  | 13 | 6 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3313 | Toshiba | R32 ESTIA Series 1 | HWT-801HRW-E + HWT-1101XWHT9W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.77 | 13.67 | 33.3 | 13.67 | HWT-801HRW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT9W-E | Back-up heater - on-board |  | 13 | 9 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3314 | Toshiba | R32 ESTIA Series 1 | HWT-1101HRW-E + HWT-1101XWHM3W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 33.3 | 7.66 | 33.3 | 7.66 | HWT-1101HRW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWT-1101XWHM3W-E | Back-up heater - on-board |  | 13 | 3 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3315 | Toshiba | R32 ESTIA Series 1 | HWT-1101HRW-E + HWT-1101XWHT6W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.43 | 10.67 | 33.3 | 10.67 | HWT-1101HRW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT6W-E | Back-up heater - on-board |  | 13 | 6 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3316 | Toshiba | R32 ESTIA Series 1 | HWT-1101HRW-E + HWT-1101XWHT9W-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.77 | 13.67 | 33.3 | 13.67 | HWT-1101HRW-E | Heat pump |  | 20.3 | 4.67 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-12 | EN 61000-3-11 | T-2069469-03_R32.pdf | T-2069469-03 | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power |  | 820 | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | HWT-1101XWHT9W-E | Back-up heater - on-board |  | 13 | 9 | DOC ATW Hydro_TCAE_PL_QD_025_R32ATW.PDF | TCAE_PL_QD_025_R32ATW | EN 61000-3-2 | EN 61000-3-3 | T-2069469-03_R32.pdf | T-2069469-03 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3317 | Toshiba | ESTIA Series 5 | HWS-805H-E + HWS-805XWHM3-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 32.2 | 7.41 | 32.2 | 7.41 | HWS-805H-E | Heat pump |  | 19.2 | 4.42 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[16 empty] | HWS-805XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3318 | Toshiba | ESTIA Series 5 | HWS-805H-E + HWS-805XWHT6-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 15.07 | 10.42 | 32.2 | 10.42 | HWS-805H-E | Heat pump |  | 19.2 | 4.42 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-805XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3319 | Toshiba | ESTIA Series 5 | HWS-805H-E + HWS-805XWHT9-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 19.4 | 13.42 | 32.2 | 13.42 | HWS-805H-E | Heat pump |  | 19.2 | 4.42 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-805XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3320 | Toshiba | ESTIA Series 5 | HWS-1105H-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 35.8 | 8.23 | 35.8 | 8.23 | HWS-1105H-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3321 | Toshiba | ESTIA Series 5 | HWS-1105H-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.24 | 35.8 | 11.24 | HWS-1105H-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3322 | Toshiba | ESTIA Series 5 | HWS-1105H-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 20.6 | 14.24 | 35.8 | 14.24 | HWS-1105H-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3323 | Toshiba | ESTIA Series 5 | HWS-1405H-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 35.8 | 8.23 | 35.8 | 8.23 | HWS-1405H-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3324 | Toshiba | ESTIA Series 5 | HWS-1405H-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.24 | 35.8 | 11.24 | HWS-1405H-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3325 | Toshiba | ESTIA Series 5 | HWS-1405H-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 20.6 | 14.24 | 35.8 | 14.24 | HWS-1405H-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3326 | Toshiba | ESTIA Series 5 | HWS-1105H8-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-1105H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3327 | Toshiba | ESTIA Series 5 | HWS-1105H8-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-1105H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3328 | Toshiba | ESTIA Series 5 | HWS-1105H8-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-1105H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3329 | Toshiba | ESTIA Series 5 | HWS-1405H8-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-1405H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3330 | Toshiba | ESTIA Series 5 | HWS-1405H8-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-1405H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3331 | Toshiba | ESTIA Series 5 | HWS-1405H8-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-1405H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3332 | Toshiba | ESTIA Series 5 | HWS-1605H8-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-1605H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3333 | Toshiba | ESTIA Series 5 | HWS-1605H8-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-1605H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3334 | Toshiba | ESTIA Series 5 | HWS-1605H8-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-1605H8-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3335 | Toshiba | ESTIA Series 5 | HWS-1105H8R-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-1105H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3336 | Toshiba | ESTIA Series 5 | HWS-1105H8R-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-1105H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3337 | Toshiba | ESTIA Series 5 | HWS-1105H8R-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-1105H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3338 | Toshiba | ESTIA Series 5 | HWS-1405H8R-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-1405H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3339 | Toshiba | ESTIA Series 5 | HWS-1405H8R-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-1405H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3340 | Toshiba | ESTIA Series 5 | HWS-1405H8R-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-1405H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3341 | Toshiba | ESTIA Series 5 | HWS-1605H8R-E + HWS-1405XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-1605H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3342 | Toshiba | ESTIA Series 5 | HWS-1605H8R-E + HWS-1405XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-1605H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3343 | Toshiba | ESTIA Series 5 | HWS-1605H8R-E + HWS-1405XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-1605H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T003728-01_3.pdf | T003728-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 710 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-1405XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf, T003728-01_3.pdf | T-1356119-01, T003728-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3344 | Toshiba | ESTIA Series 5 | HWS-P805H8R-E + HWS-P805XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-P805H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P805XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3345 | Toshiba | ESTIA Series 5 | HWS-P805H8R-E + HWS-P805XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-P805H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P805XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3346 | Toshiba | ESTIA Series 5 | HWS-P805H8R-E + HWS-P805XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-P805H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P805XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3347 | Toshiba | ESTIA Series 5 | HWS-P1105H8R-E + HWS-P1105XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-P1105H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P1105XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3348 | Toshiba | ESTIA Series 5 | HWS-P1105H8R-E + HWS-P1105XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-P1105H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P1105XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3349 | Toshiba | ESTIA Series 5 | HWS-P1105H8R-E + HWS-P1105XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-P1105H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P1105XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3350 | Toshiba | ESTIA Series 5 | HWS-P1405H8R-E + HWS-P1105XWHM3-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 18.93 | 13.12 | 27.6 | 13.12 | HWS-P1405H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P1105XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3351 | Toshiba | ESTIA Series 5 | HWS-P1405H8R-E + HWS-P1105XWHT6-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 23.27 | 16.12 | 27.6 | 16.12 | HWS-P1405H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P1105XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3352 | Toshiba | ESTIA Series 5 | HWS-P1405H8R-E + HWS-P1105XWHT9-E | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 27.6 | 19.12 | 27.6 | 19.12 | HWS-P1405H8R-E | Heat pump |  | 14.6 | 10.12 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1866033-01_Series5_3ph.pdf | T-1866033-01 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 1220 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | HWS-P1105XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 | T-1356119-01-4.pdf | T-1356119-01 | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3353 | Toshiba | ESTIA Series 5 | HWS-P805HR-E + HWS-P805XWHM3-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 35.8 | 8.23 | 35.8 | 8.23 | HWS-P805HR-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[16 empty] | HWS-P805XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3354 | Toshiba | ESTIA Series 5 | HWS-P805HR-E + HWS-P805XWHT6-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.24 | 35.8 | 11.24 | HWS-P805HR-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-P805XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3355 | Toshiba | ESTIA Series 5 | HWS-P805HR-E + HWS-P805XWHT9-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 20.6 | 14.24 | 35.8 | 14.24 | HWS-P805HR-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-P805XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3356 | Toshiba | ESTIA Series 5 | HWS-P1105HR-E + HWS-P1105XWHM3-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 35.8 | 8.23 | 35.8 | 8.23 | HWS-P1105HR-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[16 empty] | HWS-P1105XWHM3-E | Back-up heater - on-board |  | 13 | 3 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3357 | Toshiba | ESTIA Series 5 | HWS-P1105HR-E + HWS-P1105XWHT6-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.24 | 35.8 | 11.24 | HWS-P1105HR-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-P1105XWHT6-E | Back-up heater - on-board |  | 13 | 6 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3358 | Toshiba | ESTIA Series 5 | HWS-P1105HR-E + HWS-P1105XWHT9-E | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 20.6 | 14.24 | 35.8 | 14.24 | HWS-P1105HR-E | Heat pump |  | 22.8 | 5.24 | 181214_ATW_DoC_Estia.pdf | A2W-181214 | EN 61000-3-12 | EN 61000-3-11 | T-1356119-02.pdf | T-1356119-02 | No | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 28 | 0.1184 | 0.447 | Requires Service Current Capacity ≥100A per phase
[6 empty] | 3 | 400 | [8 empty] | HWS-P1105XWHT9-E | Back-up heater - on-board |  | 13 | 9 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  | No | Yes |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3401 | Bosch | Compress | CS7001iAW 5 OR-S 1ph & AWM 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 18.5 | 4.26 | 18.5 | 4.26 | CS7001iAW 5 OR-S 1ph & AWM 5-9 1ph | Whole system |  | 18.5 | 4.26 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847935 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3402 | Bosch | Compress | CS7001iAW 7 OR-S 1ph & AWM 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 22.5 | 5.18 | 22.5 | 5.18 | CS7001iAW 7 OR-S 1ph & AWM 5-9 1ph | Whole system |  | 22.5 | 5.18 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847935 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3403 | Bosch | Compress | CS7001iAW 9 OR-S 1ph & AWM 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.5 | 5.64 | 24.5 | 5.64 | CS7001iAW 9 OR-S 1ph & AWM 5-9 1ph | Whole system |  | 24.5 | 5.64 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847935 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3404 | Bosch | Compress | CS7001iAW 13 OR-S (Outdoor Unit) 1ph & AWM 13-17 (Indoor Unit) 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 33.9 | 7.8 | 33.9 | 7.8 | CS7001iAW 13 OR-S | Heat pump |  | 25.2 | 5.8 | 6720872038_Bosch_CS7001iAW_13_OR-S.pdf | 6720872038 | EN 61000-3-12 | EN 61000-3-3 | 906 AWNOR906_ANNEX to Summary_CS7001AW-1Ph-13kW_Hidria-Fan_EMC-Measurements.pdf |  | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 15 | 0.012075 | 4.381 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWM 13-17 1ph | Supplementary (boost) heater - on-board |  | 17.39 | 4 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes | 1305447 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3405 | Bosch | Compress | CS7001iAW 5 OR-S + AWM 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.25 | 22.8 | 11.25 | CS7001iAW 5 OR-S + AWM 5-9 3ph | Whole system |  | 9.8 | 2.25 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf | 6720847935 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907
HP_3406 | Bosch | Compress | CS7001iAW 7 OR-S + AWM 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 17.6 | 12.17 | 26.8 | 12.17 | CS7001iAW 7 OR-S + AWM 5-9 3ph | Whole system |  | 13.8 | 3.17 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf | 6720847935 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907
HP_3407 | Bosch | Compress | CS7001iAW 9 OR-S + AWM 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 18.27 | 12.63 | 28.8 | 12.63 | CS7001iAW 9 OR-S + AWM 5-9 3ph | Whole system |  | 15.8 | 3.63 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf | 6720847935 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3408 | Bosch | Compress | CS7001iAW 13 OR-S (Outdoor Unit) 1ph & AWM 13-17 (Indoor Unit) 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 29.53 | 14.8 | 38.2 | 14.8 | CS7001iAW 13 OR-S | Heat pump |  | 25.2 | 5.8 | 6720872038_Bosch_CS7001iAW_13_OR-S.pdf | 6720872038 | EN 61000-3-12 | EN 61000-3-3 | 906 AWNOR906_ANNEX to Summary_CS7001AW-1Ph-13kW_Hidria-Fan_EMC-Measurements.pdf |  | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 15 | 0.012075 | 4.381 | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | AWM 13-17 3ph | Supplementary (boost) heater - on-board |  | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | EN 61000-3-2 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes | 1305447 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3409 | Bosch | Compress | CS7001iAW 17 OR-T (Outdoor Unit) 3ph & AWM 13-17 (Indoor Unit) 3ph | Heating only | Air Source | 3 | 400 |  |  |  |  | 24.2 | 16.77 | 24.2 | 16.77 | CS7001iAW 17 OR-T | Heat pump |  | 11.2 | 7.76 | 6720872029_Bosch_CS7001iAW_13_OR-T_17_OR-T | 6720872029 | EN 61000-3-2 | EN 61000-3-3 | Testreport-EMC-270789-TL7-1_2020-02-28.pdf | 270789-TL7-1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | AWM 13-17 3ph | Supplementary (boost) heater - on-board |  | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | EN 61000-3-2 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes | 1305447 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3410 | Bosch | Compress | CS7001iAW 5 OR-S 1ph & AWE 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 18.5 | 4.26 | 18.5 | 4.26 | CS7001iAW 5 OR-S 1ph & AWE 5-9 1ph | Whole system |  | 18.5 | 4.26 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847935 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3411 | Bosch | Compress | CS7001iAW 7 OR-S 1ph & AWE 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 22.5 | 5.18 | 22.5 | 5.18 | CS7001iAW 7 OR-S 1ph & AWE 5-9 1ph | Whole system |  | 22.5 | 5.18 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847935 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3412 | Bosch | Compress | CS7001iAW 9 OR-S 1ph & AWE 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 24.5 | 5.64 | 24.5 | 5.64 | CS7001iAW 9 OR-S 1ph & AWE 5-9 1ph | Whole system |  | 24.5 | 5.64 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847935 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3413 | Bosch | Compress | CS7001iAW 13 OR-S (Outdoor Unit) 1ph & AWE 13-17 (Indoor Unit) 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 33.9 | 7.8 | 33.9 | 7.8 | CS7001iAW 13 OR-S | Heat pump |  | 25.2 | 5.8 | 6720872038_Bosch_CS7001iAW_13_OR-S.pdf | 6720872038 | EN 61000-3-12 | EN 61000-3-3 | 906 AWNOR906_ANNEX to Summary_CS7001AW-1Ph-13kW_Hidria-Fan_EMC-Measurements.pdf | EMC - Investigation | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 15 | 0.012075 | 4.381 | Equipment complying with IEC 61000-3-3 technical requirements
[16 empty] | AWE 13-17 1ph | Supplementary (boost) heater - on-board |  | 17.39 | 4 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes | 1305447 | Yes | Yes | Yes | [5 empty] | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3414 | Bosch | Compress | CS7001iAW 5 OR-S + AWE 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.25 | 22.8 | 11.25 | CS7001iAW 5 OR-S + AWE 5-9 3ph | Whole system |  | 9.8 | 2.25 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf | 6720847935 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3415 | Bosch | Compress | CS7001iAW 7 OR-S + AWE 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 17.6 | 12.17 | 26.8 | 12.17 | CS7001iAW 7 OR-S + AWE 5-9 3ph | Whole system |  | 13.8 | 3.17 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf | 6720847935 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3416 | Bosch | Compress | CS7001iAW 9 OR-S + AWE 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 18.27 | 12.63 | 28.8 | 12.63 | CS7001iAW 9 OR-S + AWE 5-9 3ph | Whole system |  | 15.8 | 3.63 | DoC_6720847935_Bosch_CS7000iAW 5-17 OR-S_T_20190716.pdf | 6720847935 | EN 61000-3-12 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3417 | Bosch | Compress | CS7001iAW 13 OR-S (Outdoor Unit) 1ph & AWE 13-17 (Indoor Unit) 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 29.53 | 14.8 | 38.2 | 14.8 | CS7001iAW 13 OR-S | Heat pump |  | 25.2 | 5.8 | 6720872038_Bosch_CS7001iAW_13_OR-S.pdf | 6720872038 | EN 61000-3-12 | EN 61000-3-3 | 906 AWNOR906_ANNEX to Summary_CS7001AW-1Ph-13kW_Hidria-Fan_EMC-Measurements.pdf |  | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 15 | 0.012075 | 4.381 | Equipment complying with IEC 61000-3-3 technical requirements
[6 empty] | 3 | 400 | [8 empty] | AWE13-17 3ph | Supplementary (boost) heater - on-board |  | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | EN 61000-3-2 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes | 1305447 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3418 | Bosch | Compress | CS7001iAW 17 OR-T (Outdoor Unit) 3ph & AWE 13-17 (Indoor Unit) 3ph | Heating only | Air Source | 3 | 400 |  |  |  |  | 24.2 | 16.77 | 24.2 | 16.77 | CS7001iAW 17 OR-T | Heat pump |  | 11.2 | 7.76 | 6720872029_Bosch_CS7001iAW_13_OR-T_17_OR-T | 6720872029 | EN 61000-3-2 | EN 61000-3-3 | Testreport-EMC-270789-TL7-1_2020-02-28.pdf | 270789-TL7-1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[16 empty] | AWE 13-17 3ph | Supplementary (boost) heater - on-board |  | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | EN 61000-3-2 | EN 61000-3-3 | Report 1305447D_ed2 AirX50-90+all Airboxes | 1305447 | Yes | Yes | Yes | [5 empty] | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3419 | Bosch | Compress | CS7400iAW 5 OR 1ph & AWM 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 18.5 | 4.26 | 18.5 | 4.26 | CS7400iAW 5 OR 1ph & AWM 5-9 1ph | Whole system |  | 18.5 | 4.26 | DoC_6720872025_Bosch_CS7400i_AW.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720872025 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3420 | Bosch | Compress | CS7400iAW 7 OR 1ph & AWM 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 22.5 | 5.18 | 22.5 | 5.18 | CS7400iAW 7 OR 1ph & AWM 5-9 1ph | Whole system |  | 22.5 | 5.18 | DoC_6720872025_Bosch_CS7400i_AW.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720872025 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3421 | Bosch | Compress | CS7400iAW 5 OR 1ph & AWM 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.25 | 22.8 | 11.25 | CS7400iAW 5 OR 1ph & AWM 5-9 3ph | Whole system |  | 9.8 | 2.25 | DoC_6720872025_Bosch_CS7400i_AW.pdf | 6720872025 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3422 | Bosch | Compress | CS7400iAW 7 OR 1ph & AWM 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 17.6 | 12.17 | 26.8 | 12.17 | CS7400iAW 7 OR 1ph & AWM 5-9 3ph | Whole system |  | 13.8 | 3.17 | DoC_6720872025_Bosch_CS7400i_AW.pdf | 6720872025 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3423 | Bosch | Compress | CS7400iAW 5 OR 1ph & AWE 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 18.5 | 4.26 | 18.5 | 4.26 | CS7400iAW 5 OR 1ph & AWE 5-9 1ph | Whole system |  | 18.5 | 4.26 | DoC_6720872025_Bosch_CS7400i_AW.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720872025 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3424 | Bosch | Compress | CS7400iAW 7 OR 1ph & AWE 5-9 1ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 22.5 | 5.18 | 22.5 | 5.18 | CS7400iAW 7 OR 1ph & AWE 5-9 1ph | Whole system |  | 22.5 | 5.18 | DoC_6720872025_Bosch_CS7400i_AW.pdf & DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720872025 & 6720847907 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3425 | Bosch | Compress | CS7400iAW 5 OR 1ph & AWE 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 16.27 | 11.25 | 22.8 | 11.25 | CS7400iAW 5 OR 1ph & AWE 5-9 3ph | Whole system |  | 9.8 | 2.25 | DoC_6720872025_Bosch_CS7400i_AW.pdf | 6720872025 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3426 | Bosch | Compress | CS7400iAW 7 OR 1ph & AWE 5-9 3ph | Heating only | Air Source | 1 | 230 |  |  |  |  | 17.6 | 12.17 | 26.8 | 12.17 | CS7400iAW 7 OR 1ph & AWE 5-9 3ph | Whole system |  | 13.8 | 3.17 | DoC_6720872025_Bosch_CS7400i_AW.pdf | 6720872025 | EN 61000-3-12 | EN 61000-3-3 | 190800228_EMC2.pdf & 190800228_Annex_A.pdf & Report 1305447D_ed2 AirX50-90+all Airboxes.pdf | 190800228 & 1305477D Ed 2 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[6 empty] | 3 | 400 | [11 empty] | 13 | 9 | DoC_6720847907_Bosch_ AWM AWB AWE _20190716.pdf | 6720847907 | [15 empty] | N/A | N/A | N/A
HP_3427 | Bosch | CS5000 AW | CS5000 AW 38 O | Heating only | Air Source | 3 | 400 |  |  |  |  | 47.63 | 33 | 47.63 | 33 | CS5000 AW 38 O | Heat pump |  | 47.63 | 33 | 6720872049_Bosch_Compress_5000_AW_17-38_O_OR.pdf | 6720872049 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_282443_TL7_1_2021-06-11_282443-TL7-1 G_-6BAACAAF0048 | 282443-TL7-1 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.504 | 0.317 | Requires Zsource ≤Zmax | 0.2192
HP_3428 | Bosch | CS5000 AW | CS5000 AW 38 OR | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 47.63 | 33 | 47.63 | 33 | CS5000 AW 38 OR | Heat pump |  | 47.63 | 33 | 6720872049_Bosch_Compress_5000_AW_17-38_O_OR.pdf | 6720872049 | EN 61000-3-12 | EN 61000-3-11 | VDE_Test-Report_EMC_282443_TL7_1_2021-06-11_282443-TL7-1 G_-6BAACAAF0048 | 282443-TL7-1 | No | No | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | 19 | 0.504 | 0.317 | Requires Zsource ≤Zmax | 0.2192
HP_3429 | Bosch | CS5000 AW | CS5000 AW 22 O | Heating only | Air Source | 3 | 400 |  |  |  |  | 22.55 | 15.63 | 22.55 | 15.63 | CS5000AW 22 O | Heat pump |  | 22.55 | 15.63 | 6720872049_Bosch_Compress_5000_AW_17-38_O_OR.pdf | 6720872049 | EN 61000-3-12 | EN 61000-3-11 | 2021-0071-EMC-TR-22-0100-V02_Glen Dimplex_LA 35TBS_CE | 21-0100 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Not applicable
HP_3601 | Riello | NXHM 004 | 20191936 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.1 | 2.323 | 10.1 | 2.323 | 20191936 | Heat pump |  | 10.1 | 2.3 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-2 | EN 61000-3-3 | 64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3602 | Riello | NXHM 006 | 20191940 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.9 | 2.737 | 11.9 | 2.737 | 20191940 | Heat pump |  | 11.9 | 2.7 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-2 | EN 61000-3-3 | 64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3603 | Riello | NXHM 008 | 20191942 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.9 | 3.427 | 14.9 | 3.427 | 20191942 | Heat pump |  | 14.9 | 3.4 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-2 | EN 61000-3-3 | 64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3604 | Riello | NXHM 010 | 20191943 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.2 | 3.726 | 16.2 | 3.726 | 20191943 | Heat pump |  | 16.2 | 2.7 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-2 | EN 61000-3-3 | 64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3605 | Riello | NXHM 012 | 20191944 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.2 | 5.566 | 24.2 | 5.566 | 20191944 | Heat pump |  | 24.2 | 5.5 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3606 | Riello | NXHM 012T | 20191947 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 7.94 | 5.5 | 7.94 | 5.5 | 20191947 | Heat pump |  | 7.94 | 5.5 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-2 | EN 61000-3-3 | 64.711.18.05282.04-report | 64.711.18.05282.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3607 | Riello | NXHM 014 | 20191945 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25.22 | 5.8 | 25.22 | 5.8 | 20191945 | Heat pump |  | 25.22 | 5.8 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3608 | Riello | NXHM 014T | 20191948 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.37 | 5.8 | 8.37 | 5.8 | 20191948 | Heat pump |  | 8.37 | 5.8 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-2 | EN 61000-3-3 | 64.711.18.05282.04-report | 64.711.18.05282.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3609 | Riello | NXHM 016 | 20191946 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 26.96 | 6.2 | 26.96 | 6.2 | 20191946 | Heat pump |  | 26.96 | 6.2 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3610 | Riello | NXHM 016T | 20191949 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.95 | 6.2 | 8.95 | 6.2 | 20191949 | Heat pump |  | 8.95 | 6.2 | Declaration of conformity_NXHM 004-016 (1) |  | EN 61000-3-2 | EN 61000-3-3 | 64.711.18.05282.04-report | 64.711.18.05282.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3701 | Trianco | Activair | Activair 7kW | Heating & Cooling | Air Source | 1 | 230 |  | 6.51 |  |  | 8.7 | 1.92 | 8.7 | 1.92 | Activair 7kW | Heat pump |  | 8.7 | 1.92 | 64711220109502UK CERT_EMC | 64711220109502UK | EN 61000-3-2 | EN 61000-3-3 | 64711220109502UK TRF_EMC | 64.711.22.01095.02UK | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3702 | Trianco | Activair | Activair 12kW | Heating & Cooling | Air Source | 1 | 230 |  | 11.72 |  |  | 15.3 | 3.37 | 15.3 | 3.37 | Activair 12kW | Heat pump |  | 15.3 | 3.37 | 64711220109502UK CERT_EMC | 64711220109502UK | EN 61000-3-2 | EN 61000-3-3 | 64711220109502UK TRF_EMC | 64.711.22.01095.02UK | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3801 | Airwell | AW-WHPMA04-H91 | 7HP061075 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.1 | 2.32 | 10.1 | 2.32 | 7HP061075 | Heat pump |  | 10.1 | 2.32 | 22.AW.CE.WHPMA4-10.01.06 |  | EN 61000-3-2 | EN 61000-3-3 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3802 | Airwell | AW-WHPMA06-H91 | 7HP061076 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.9 | 2.74 | 11.9 | 2.74 | 7HP061076 | Heat pump |  | 11.9 | 2.74 | 22.AW.CE.WHPMA4-10.01.06 |  | EN 61000-3-2 | EN 61000-3-3 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3803 | Airwell | AW-WHPMA08-H91 | 7MB140001 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.9 | 3.43 | 14.9 | 3.43 | 7MB140001 | Heat pump |  | 14.9 | 3.43 | 22.AW.CE.WHPMA4-10.01.06 |  | EN 61000-3-2 | EN 61000-3-3 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3804 | Airwell | AW-WHPMA08-H91 | 7HP061077 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 27.9 | 6.42 | 27.9 | 6.42 | 7HP061077 | Whole system |  | 27.9 | 6.42 | 22.AW.CE.WHPMA4-10.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3805 | Airwell | AW-WHPMA10-H91 | 7MB140002 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.2 | 3.73 | 16.2 | 3.73 | 7MB140002 | Heat pump |  | 16.2 | 3.73 | 22.AW.CE.WHPMA4-10.01.06 |  | EN 61000-3-2 | EN 61000-3-3 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3806 | Airwell | AW-WHPMA10-H91 | 7HP061078 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 29.2 | 6.72 | 29.2 | 6.72 | 7HP061078 | Whole system |  | 29.2 | 6.72 | 22.AW.CE.WHPMA4-10.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3807 | Airwell | AW-WHPMA12-H91 | 7MB140003 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.2 | 5.57 | 24.2 | 5.57 | 7MB140003 | Heat pump |  | 24.2 | 5.57 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A and MHC-V8(10)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3808 | Airwell | AW-WHPMA12-H91 | 7HP061079 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 37.2 | 8.56 | 37.2 | 8.56 | 7HP061079 | Whole system |  | 37.2 | 8.56 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05282.04-report | 64.711.18.05282.04-(E) | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3809 | Airwell | AW-WHPMA12-H93 | 7MB140006 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 7.94 | 5.5 | 7.94 | 5.5 | 7MB140006 | Heat pump |  | 7.94 | 5.5 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-2 | EN 61000-3-3 | MHC-V8(10)WD2N8-B & PD25320Q62 MHC-V8W$D2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3810 | Airwell | AW-WHPMA12-H93 | 7HP061082 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 20.94 | 14.51 | 20.94 | 14.51 | 7HP061082 | Whole system |  | 20.94 | 14.51 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05282.04-report | 64.711.18.05282.04-(E) | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3811 | Airwell | AW-WHPMA14-H91 | 7MB140004 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25.22 | 5.8 | 25.22 | 5.8 | 7MB140004 | Heat pump |  | 25.22 | 5.8 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A and MHC-V8(10)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3812 | Airwell | AW-WHPMA14-H91 | 7HP061080 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 38.22 | 8.79 | 38.22 | 8.79 | 7HP061080 | Whole system |  | 38.22 | 8.79 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05282.04-report | 64.711.18.05282.04-(E) | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3813 | Airwell | AW-WHPMA14-H93 | 7MB140007 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.37 | 5.799 | 8.37 | 5.799 | 7MB140007 | Heat pump |  | 8.37 | 5.799 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3814 | Airwell | AW-WHPMA14-H93 | 7HP061083 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21.37 | 14.81 | 21.37 | 14.81 | 7HP061083 | Whole system |  | 21.37 | 14.81 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05282.04-report | 64.711.18.05282.04-(E) | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3815 | Airwell | AW-WHPMA16-H91 | 7MB140005 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 26.96 | 6.2 | 26.96 | 6.2 | 7MB140005 | Heat pump |  | 26.96 | 6.2 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A and MHC-V8(10)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3816 | Airwell | AW-WHPMA16-H91 | 7HP061081 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 39.96 | 9.92 | 39.96 | 9.92 | 7HP061081 | Whole system |  | 39.96 | 9.92 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05282.04-report | 64.711.18.05282.04-(E) | No | Yes | No | No | No | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3817 | Airwell | AW-WHPMA16-H93 | 7MB140008 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.95 | 6.2 | 8.95 | 6.2 | 7MB140008 | Heat pump |  | 8.95 | 6.2 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3818 | Airwell | AW-WHPMA16-H93 | 7HP061084 | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 21.95 | 15.21 | 21.95 | 15.21 | 7HP061084 | Whole system |  | 21.95 | 15.21 | 22.AW.CE.WHPMA12-16.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.18.05282.04-report | 64.711.18.05282.04-(E) | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3819 | Airwell | AW-WHPMA18-H93 | 7HP061085 | Heating only | Air Source | 3 | 400 |  |  |  |  | 17 | 11.7779 | 17 | 11.7779 | 7HP061085 | Heat pump |  | 17 | 11.7779 | 22.AW.CE.WHPMA18-30.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.19.06744.01-report | 64.711.19.06744.01- (E) | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4123 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3820 | Airwell | AW-WHPMA22-H93 | 7HP061086 | Heating only | Air Source | 3 | 400 |  |  |  |  | 20 | 13.86 | 20 | 13.86 | 7HP061086 | Heat pump |  | 20 | 13.86 | 22.AW.CE.WHPMA18-30.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.19.06744.01-report | 64.711.19.06744.01- (E) | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 4851 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3821 | Airwell | AW-WHPMA26-H93 | 7HP061087 | Heating only | Air Source | 3 | 400 |  |  |  |  | 22 | 15.24 | 22 | 15.24 | 7HP061087 | Heat pump |  | 22 | 15.24 | 22.AW.CE.WHPMA18-30.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.19.06744.01-report | 64.711.19.06744.01- (E) | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 5334 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3822 | Airwell | AW-WHPMA30-H93 | 7HP061088 | Heating only | Air Source | 3 | 400 |  |  |  |  | 23 | 15.93 | 23 | 15.93 | 7HP061088 | Heat pump |  | 23 | 15.93 | 22.AW.CE.WHPMA18-30.01.06 |  | EN 61000-3-12 | EN 61000-3-11 | 64.711.19.06744.01-report | 64.711.19.06744.01- (E) | No | Yes | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | 5577 |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3901 | Clivet | WISAN-YME 1 S 2.1 | WISAN-YME 1 S 2.1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.1 | 2.32 | 10.1 | 2.32 | WISAN-YME 1 S 2.1 | Heat pump |  | 10.1 | 2.32 | CE Certificate 2.1 - 5.1 |  | EN 61000-3-2 | EN 61000-3-3 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 - (E) | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3902 | Clivet | WISAN-YME 1 S 3.1 | WISAN-YME 1 S 3.1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.9 | 2.74 | 11.9 | 2.74 | WISAN-YME 1 S 3.1 | Heat pump |  | 11.9 | 2.74 | CE Certificate 2.1 - 5.1 |  | EN 61000-3-2 | EN 61000-3-3 | CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 | 64.711.18.05280.04 - (E) | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3903 | Clivet | WISAN-YME 1 S 4.1 | WISAN-YME 1 S 4.1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.9 | 3.43 | 14.9 | 3.43 | WISAN-YME 1 S 4.1 | Heat pump |  | 14.9 | 3.43 | CE Certificate 2.1 - 5.1 |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V8W$D2RN8-B & MHC-V8(10)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3904 | Clivet | WISAN-YME 1 S 5.1 | WISAN-YME 1 S 5.1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16.2 | 3.73 | 16.2 | 3.73 | WISAN-YME 1 S 5.1 | Heat pump |  | 16.2 | 3.73 | CE Certificate 2.1 - 5.1 |  | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V8W$D2RN8-B & MHC-V8(10)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_3905 | Clivet | WISAN-YME 1 S 6.1 | WISAN-YME 1 S 6.1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.2 | 5.57 | 24.2 | 5.57 | WISAN-YME 1 S 6.1 | Heat pump |  | 24.2 | 5.57 | CE Certificate WiSAN-YME 6.1 |  | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3906 | Clivet | WISAN-YME 1 S 7.1 | WISAN-YME 1 S 7.1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25.22 | 5.8 | 25.22 | 5.8 | WISAN-YME 1 S 7.1 | Heat pump |  | 25.22 | 5.8 | CE Certificate WiSAN-YME 7.1 |  | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_3907 | Clivet | WISAN-YME 1 S 8.1 | WISAN-YME 1 S 8.1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 26.96 | 6.2 | 26.96 | 6.2 | WISAN-YME 1 S 8.1 | Heat pump |  | 26.96 | 6.2 | CE Certificate WiSAN-YME 8.1 |  | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4001 | Immergas | Magis M4 | Magis M4 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.1 | 2.3 | 10.1 | 2.3 | Magis M4 | Heat pump | 3.0324 | 10.1 | 2.3 | EU DECLARATION OF CONFORMITY | N. 420622.000 -EN | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V6W$D2RN8-B & CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4002 | Immergas | Magis M6 | Magis M6 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 11.9 | 2.7 | 11.9 | 2.7 | Magis M6 | Heat pump | 3.0324 | 11.9 | 2.7 | EU DECLARATION OF CONFORMITY | N. 420622.000 -EN | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V6W$D2RN8-B & CE certificate & Reports4-16kW 1p64.711.18.05280.04 TRF_EMC R32 Monobloc 单相单风轮机型 |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4003 | Immergas | Magis M8 | Magis M8 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14.9 | 3.4 | 14.9 | 3.4 | Magis M8 | Heat pump | 3.0324 | 14.9 | 3.4 | EU DECLARATION OF CONFORMITY | N. 420622.000 -EN | EN 61000-3-2 | EN 61000-3-3 | PD25320Q62 MHC-V8W$D2RN8-B & MHC-V8(10)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4004 | Immergas | Magis M12 | Magis M12 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 24.2 | 5.5 | 24.2 | 5.5 | Magis M12 | Heat pump | 3.0324 | 24.2 | 5.5 | EU DECLARATION OF CONFORMITY | N. 410622.000 -EN | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4005 | Immergas | Magis M14 | Magis M14 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 25.22 | 5.8 | 25.22 | 5.8 | Magis M14 | Heat pump | 3.0324 | 25.22 | 5.8 | EU DECLARATION OF CONFORMITY | N. 410622.000 -EN | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4006 | Immergas | Magis M16 | Magis M16 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 26.96 | 6.2 | 26.96 | 6.2 | Magis M16 | Heat pump | 3.0324 | 26.96 | 6.2 | EU DECLARATION OF CONFORMITY | N. 410622.000 -EN | EN 61000-3-12 | EN 61000-3-11 | CE-LRSJ-V160 Harmonic 25A & MHC-V12(14,16)WD2N8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4007 | Immergas | Magis M12T | Magis M12T | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 7.94 | 5.5 | 7.94 | 5.5 | Magis M12T | Heat pump | 3.0324 | 7.94 | 5.5 | EU DECLARATION OF CONFORMITY | N. 410622.000 -EN | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4008 | Immergas | Magis M14T | Magis M14T | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.37 | 5.8 | 8.37 | 5.8 | Magis M14T | Heat pump | 3.0324 | 8.37 | 5.8 | EU DECLARATION OF CONFORMITY | N. 410622.000 -EN | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4009 | Immergas | Magis M16T | Magis M16T | Heating & Cooling | Air Source | 3 | 400 |  |  |  |  | 8.95 | 6.2 | 8.95 | 6.2 | Magis M16T | Heat pump | 3.0324 | 8.95 | 6.2 | EU DECLARATION OF CONFORMITY | N. 410622.000 -EN | EN 61000-3-2 | EN 61000-3-3 | PD25320Q63 MHC-V16W$D2RN8-B & MHC-V12(14,16)WD2RN8-B |  | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4010 | Alpha | Hydro 5kW | Hyrdo 5kW | Heating only | Air Source | 1 | 230 |  |  | 12.65 |  | 16 | 3.68 | 16 | 3.68 | Hydro 5kW | Whole system |  | 16 | 3.68 | 19032_CE DoC AE050RXYDEG_Rev00 |  | EN 61000-3-2 | EN 61000-3-3 | ECE-2019-000022_Rv1 | ECE-2019-000022 | Yes | Yes | Yes | Yes | Yes | Yes | No | 1.SSEC_EHS_R-32_OUT_MONO_EU_IM_DB68-08368A-00_EN_20190409 | Not applicable |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4011 | Alpha | Hydro 8kW | Hyrdo 8kW | Heating only | Air Source | 1 | 230 |  |  | 17.43 |  | 22 | 5.06 | 22 | 5.06 | Hydro 8kW | Whole system |  | 22 | 5.06 | 19033_CE DoC AE080RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000023_Rv1 | ECE-2019-000023 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4012 | Alpha | Hydro 12kW | Hyrdo 12kW | Heating only | Air Source | 1 | 230 |  |  | 29.74 |  | 28 | 6.44 | 28 | 6.44 | Hydro 12kW | Whole system |  | 28 | 6.44 | 19035_CE DoC AE160RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000024_Rv1 | ECE-2019-000024 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4013 | Alpha | Hydro 16kW | Hyrdo 16kW | Heating only | Air Source | 1 | 230 |  |  | 35.09 |  | 32 | 7.36 | 32 | 7.36 | Hydro 16kW | Whole system |  | 32 | 7.36 | 19035_CE DoC AE160RXYDEG_Rev00 |  | EN 61000-3-12 | EN 61000-3-11 | ECE-2019-000024_Rv1 | ECE-2019-000024 | Yes | Yes | Yes | Yes | Yes | Yes | No | EHS_R-32_MONO_IM_EN_DB68-08408A-00_190502 | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4014 | Alpha | E-Tec Hybrid | E-Tec Hybrid | Heating only | Air Source | 1 | 230 |  |  |  |  | 15.7 | 3.611 | 15.7 | 3.611 | E-Tec Hybrid | Heat pump |  | 15.7 | 3.611 | 4.EJHA04AAV3_DoC14W900-2AF.pdf | DoC14W900-2AF | EN 61000-3-2 | EN 61000-3-3 | 2230920.0501-EMC | 2230920.0501-EMC | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4101 | Acond | PRO-N | PRO-N | Heating only | Air Source | 1 | 230 |  |  |  |  | 13 | 2.99 | 13 | 2.99 | PRO-N | Heat pump |  | 13 | 2.99 | cert 02035-20 rev 1.pdf | EMC-B-02035-20-rev. 1 | EN 61000-3-2 | EN 61000-3-3 | 30-15868-3-emc corrected.pdf | 30-15868-3-emc corrected | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4102 | Acond | PRO-R | PRO-R | Heating only | Air Source | 3 | 400 |  |  |  |  | 12 | 8.31 | 12 | 8.31 | PRO-R | Heat pump |  | 12 | 8.31 | cert 02035-20 rev 1.pdf | EMC-B-02035-20-rev. 1 | EN 61000-3-2 | EN 61000-3-3 | 30-15868-3-emc corrected.pdf | 30-15868-3-emc corrected | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4103 | Acond | PRO-R SP | PRO-R SP | Heating only | Air Source | 1 | 230 |  |  |  |  | 26 | 5.98 | 26 | 5.98 | PRO-R SP | Heat pump |  | 26 | 5.98 | cert 02035-20 rev 1.pdf | EMC-B-02035-20-rev. 1 | EN 61000-3-12 | EN 61000-3-11 | 30-15868-3-emc corrected.pdf | 30-15868-3-emc | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Equipment complying with IEC 61000-3-3 technical requirements
HP_4201 | Hunan Harnitek | YHPK-06V1TBA | YHPK-06V1TBA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10 | 2.3 | 10 | 2.3 | YHPK-06V1TBA | Heat pump |  | 10 | 2.3 | 64711200113802D CERT_EMC | 64711200113802D | EN 61000-3-2 | EN 61000-3-3 | 64711200113802D TRF_EMC.pdf | 64.711.20.01138.02D | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4202 | Hunan Harnitek | YHPK-09V1TBA | YHPK-09V1TBA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 14 | 3.22 | 14 | 3.22 | YHPK-09V1TBA | Heat pump |  | 14 | 3.22 | 64711200113802D CERT_EMC | 64711200113802D | EN 61000-3-2 | EN 61000-3-3 | 64711200113802D TRF_EMC.pdf | 64.711.20.01138.02D | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4203 | Hunan Harnitek | YHPK-12V1TBA | YHPK-12V1TBA | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 16 | 3.68 | 16 | 3.68 | YHPK-12V1TBA | Heat pump |  | 16 | 3.68 | 64711200113802D CERT_EMC | 64711200113802D | EN 61000-3-2 | EN 61000-3-3 | 64711200113802D TRF_EMC.pdf | 64.711.20.01138.02D | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
[17 empty] | Back-up heater - on-board |  | 13 | 2.99 |  |  | EN 61000-3-2 | EN 61000-3-3 |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
HP_4301 | Hisense | AHZ-080HCDS1 | AHZ-080HCDS1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 17.53 | 4.03 | 17.53 | 4.03 | AHZ-080HCDS1 | Heat pump |  | 17.53 | 4.03 | EU DECLARATION OF CONFORMITY-Hisense-Monobloc |  | EN 61000-3-12 | EN 61000-3-11 | BXH-ESH-P21100151B | BXH-ESH-P21100151B | Yes | No | No | No | Yes | No | Yes |  | Equipment complying with IEC 61000-3-12 |  |  | N/A | N/A | N/A | Requires Service Current Capacity ≥100A per phase | 0.35
HP_4302 | Hisense | AHZ-044HCDS1 | AHZ-044HCDS1 | Heating & Cooling | Air Source | 1 | 230 |  |  |  |  | 10.53 | 2.42 | 10.53 | 2.42 | AHZ-044HCDS1 | Heat pump |  | 10.53 | 2.42 | EU DECLARATION OF CONFORMITY-Hisense-Monobloc |  | EN 61000-3-2 | EN 61000-3-3 | BXH-ESH-P21100151B | BXH-ESH-P21100151B | Yes | Yes | Yes | Yes | Yes | Yes | No |  | Not applicable |  |  | N/A | N/A | N/A | Not applicable
Note 1: The heating module is switched on independently and does not operate in conjunction with the heat pump. The flicker calculation is based on either a 3kW, 6kW, or 9kW heating element switching in all at once i.e. not staged switching. It is assumed the harmonics are compliant to EN 61000-3-2 as the heating elements are resistive devices and therefore produce very little to no harmonics.
Drop-down lists…
|  |  |  | Heating only | Air Source | 1 | 230 | [9 empty] | Whole system | [5 empty] | EN 61000-3-12 | EN 61000-3-11 |  |  | Yes | Yes | [6 empty] | Equipment complying with IEC 61000-3-12 | [5 empty] | Equipment complying with IEC 61000-3-3 technical requirements |  | Yes | Yes |  | Yes | Yes |  | Yes | Yes
|  |  |  | Heating & Cooling | Ground Source | Split | 400 | [9 empty] | Heat pump | [5 empty] | EN 61000-3-2 | EN 61000-3-3 |  |  | No | No | [6 empty] | Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power | [5 empty] | Requires Zsource ≤Zmax |  | No | No |  | No | No |  | No | No
[5 empty] | Water Source | 3 | [10 empty] | Back-up heater - on-board | [5 empty] | EN 61000-6-3 | EN 61000-6-3 |  |  | Unknown | Unknown | [6 empty] | Not applicable | [5 empty] | Requires Service Current Capacity ≥100A per phase
[17 empty] | Back-up heater - external | [5 empty] | EN 61000-6-4 | EN 61000-6-4 | [16 empty] | Not applicable
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external
Note on M235: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M237: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M239: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M241: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M243: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M245: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M247: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M249: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M251: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M253: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M255: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M257: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on M265: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M267: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M269: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M271: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M273: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M275: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M313: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M315: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M317: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M319: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M321: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M323: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M325: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M327: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M329: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M331: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M333: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M335: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M337: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M339: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M341: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M343: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M345: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M347: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M349: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M351: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M353: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M355: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M357: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M359: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M361: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M363: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M365: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M367: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M369: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M371: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on M1409: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1411: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1415: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1417: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1421: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1423: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1483: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1489: Asad Ali: Sum of three phase current and single phase current convertered to three phase current.
Note on M1594: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O1: Scarbro, Simon P.: In the absence of data these have been set equal to the Total System (Inpu) Rated Current.
Note on O235: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O237: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O239: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O241: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O243: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O245: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O247: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O249: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O251: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O253: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O255: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O257: Asad Ali: Note: The heater does not operate when the heat pump is operational.
Note on O265: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O267: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O269: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O271: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O273: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O275: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O313: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O315: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O317: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O319: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O321: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O323: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O325: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O327: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O329: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O331: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O333: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O335: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O337: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O339: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O341: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O343: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O345: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O347: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O349: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O351: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O353: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O355: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O357: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O359: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O361: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O363: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O365: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O367: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O369: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O371: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on O1409: Asad Ali: Total current for the worst loaded phase
Note on O1411: Asad Ali: Total current for the worst loaded phase
Note on O1415: Asad Ali: Total current for the worst loaded phase
Note on O1417: Asad Ali: Total current for the worst loaded phase
Note on O1421: Asad Ali: Total current for the worst loaded phase
Note on O1423: Asad Ali: Total current for the worst loaded phase
Note on O1483: Asad Ali: Total current for the worst loaded phase
Note on O1489: Asad Ali: Total current for the worst loaded phase
Note on O1594: Asad Ali: Note: The heater does not operate when the heat pump is operational
Note on P812: John Felgate: 8.4kW compressor 3.0kW booster (including power factor of 1.1 for the motors)
Note on P813: John Felgate: 8.4kW compressor 3.0kW booster (including power factor of 1.1 for the motors)
Note on R1: Asad Ali: See * below regarding back-up heaters
Note on R1082: Asad Ali: Single phase immersion heater
Note on R1085: Asad Ali: Single phase immersion heater
Note on R1088: Asad Ali: Single phase immersion heater
Note on Y637: Asad Ali: Ztest of 0.25 + j0.25 used.
Note on AB5: Scarbro, Simon P.: Assumed.
Note on AB7: Scarbro, Simon P.: Assumed.
Note on AB11: Scarbro, Simon P.: Assumed.
Note on AC5: Scarbro, Simon P.: Assumed
Note on AC7: Scarbro, Simon P.: Assumed.
Note on AC11: Scarbro, Simon P.: Assumed.
Note on AC811: Scarbro, Simon P.: Assumed.

## A2_Data_=<16A
A2 DATA ENTRY SHEET - ≤16A
NOTE | Use this sheet to provide information for equipment compliant with IEC 61000-3-2 and IEC 61000-3-3.
DATA
Equipment
Make
Model
Model Reference
Heat Pump Type
Phases
Voltage (V)
Total Heat Pump System (Input) Rated Current (A)
Total Heat Pump System (Input) Rated Power (kVA)
Module
Module Input Rated Current (A)
Module Input Rated Power (kVA)
Declaration of Conformity
CE Declaration of Conformity Filename
CE Declaration of Conformity Document/Certificate Number
Standards Cited on CE Declaration of Conformity
Harmonic Standards
Voltage Fluctuation/Flicker Standards
Manufacturer's EMC Test Report Filename
Manufacturer's EMC Test Report Document Number
Drop-down lists
Air Source
Ground Source
Water Source
1
Split
3
230
400
Whole system
Heat pump
Back-up heater - on-board
Back-up heater - external
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external
EN 61000-3-12
EN 61000-3-2
EN 61000-6-3
EN 61000-6-4
EN 61000-3-11
EN 61000-3-3
EN 61000-6-3
EN 61000-6-4

## A3_Data_=<75A_Harmonics
A3 DATA ENTRY SHEET - ≤75A [Harmonics]
NOTE | Use this sheet to provide information and data for equipment falling within the scope of IEC 61000-3-12. This sheet is provided for all equipment types except those meeting Table 5 specified conditions (d), (e) and (f) in IEC 61000-3-12.
NOTE | To enable the Network Operator to offer the most economic electrical connection design to the connectee, it is necessary for the equipment manufacturer to provide the EMC test results against IEC 61000-3-12.
CONFIDENTIAL DATA
Equipment
Make
Model
Model Reference
Heat Pump Type
Phases
Voltage (V)
Total Heat Pump System (Input) Rated Current (A)
Total Heat Pump System (Input) Rated Power (kVA)
Module
Module Input Rated Current (A)
Module Input Rated Power (kVA)
Harmonic Current Emission Data
Phase | L1 |  | Phase | L2 |  | Phase | L3
| Current (A) |  |  | Current (A) |  |  | Current (A)
Iequ |  |  | Iequ |  |  | Iequ
Iref |  |  | Iref |  |  | Iref
| Current (A) | Ih/Iref (%) |  | Current (A) | Ih/Iref (%) |  | Current (A) | Ih/Iref (%)
RMS |  |  | RMS |  |  | RMS
Harmonic h | Ih (A) | Ih/Iref (%) | Harmonic h | Ih (A) | Ih/Iref (%) | Harmonic h | Ih (A) | Ih/Iref (%)
2 |  |  | 2 |  |  | 2
3 |  |  | 3 |  |  | 3
4 |  |  | 4 |  |  | 4
5 |  |  | 5 |  |  | 5
6 |  |  | 6 |  |  | 6
7 |  |  | 7 |  |  | 7
8 |  |  | 8 |  |  | 8
9 |  |  | 9 |  |  | 9
10 |  |  | 10 |  |  | 10
11 |  |  | 11 |  |  | 11
12 |  |  | 12 |  |  | 12
13 |  |  | 13 |  |  | 13
| THC/Iref (%) |  |  | THC/Iref (%) |  |  | THC/Iref (%)
THC |  |  | THC |  |  | THC
| PWHC/Iref (%) |  |  | PWHC/Iref (%) |  |  | PWHC/Iref (%)
PWHC |  |  | PWHC |  |  | PWHC
Manufacturer's EMC Test Report Filename
Manufacturer's EMC Test Report Document Number
Manufacturer's Documentation Declaration
In accordance with EN 61000-3-12… | [5 empty] | Minimum short-circuit level, Ssc min (kVA)
Declaration of Conformity
CE Declaration of Conformity Filename
CE Declaration of Conformity Document/Certificate Number
Standards Cited on CE Declaration of Conformity
Harmonic Standards
Voltage Fluctuation/Flicker Standards
Manufacturer's Declaration for Connection Design Purposes
Statement
Drop-down lists
Air Source
Ground Source
Water Source
1
Split
3
230
400
Whole system
Heat pump
Back-up heater - on-board
Back-up heater - external
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external
Equipment complying with IEC 61000-3-12
Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power
EN 61000-3-12
EN 61000-3-2
EN 61000-6-3
EN 61000-6-4
EN 61000-3-11
EN 61000-3-3
EN 61000-6-3
EN 61000-6-4
Emissions do not exceed Class A limits in IEC 61000-3-2
Note on D90: Scarbro, Simon P.: Use Sheet A8 to provide supporting current emission data.

## A4_Data_=<75A_def_Harmonics
A4 DATA ENTRY SHEET - ≤75A (d/e/f) [Harmonics]
NOTE | Use this sheet to provide information and data for equipment falling within the scope of IEC 61000-3-12. This sheet is provided for equipment types meeting Table 5 specified conditions (d), (e) and (f) in IEC 61000-3-12.
NOTE | To enable the Network Operator to offer the most economic electrical connection design to the connectee, it is necessary for the equipment manufacturer to provide the EMC test results against IEC 61000-3-12.
CONFIDENTIAL DATA
Equipment
Make
Model
Model Reference
Heat Pump Type
Phases
Voltage (V)
Total Heat Pump System (Input) Rated Current (A)
Total Heat Pump System (Input) Rated Power (kVA)
Module
Module Input Rated Current (A)
Module Input Rated Power (kVA)
Harmonic Current Emission Data
Phase | L1 |  | Phase | L2 |  | Phase | L3
| Current (A) |  |  | Current (A) |  |  | Current (A)
Iequ |  |  | Iequ |  |  | Iequ
Iref |  |  | Iref |  |  | Iref
| Current (A) | Ih/Iref (%) |  | Current (A) | Ih/Iref (%) |  | Current (A) | Ih/Iref (%)
RMS |  |  | RMS |  |  | RMS
Harmonic h | Ih (A) | Ih/Iref (%) | Harmonic h | Ih (A) | Ih/Iref (%) | Harmonic h | Ih (A) | Ih/Iref (%)
2 |  |  | 2 |  |  | 2
3 |  |  | 3 |  |  | 3
4 |  |  | 4 |  |  | 4
5 |  |  | 5 |  |  | 5
6 |  |  | 6 |  |  | 6
7 |  |  | 7 |  |  | 7
8 |  |  | 8 |  |  | 8
9 |  |  | 9 |  |  | 9
10 |  |  | 10 |  |  | 10
11 |  |  | 11 |  |  | 11
12 |  |  | 12 |  |  | 12
13 |  |  | 13 |  |  | 13
14 |  |  | 14 |  |  | 14
15 |  |  | 15 |  |  | 15
16 |  |  | 16 |  |  | 16
17 |  |  | 17 |  |  | 17
18 |  |  | 18 |  |  | 18
19 |  |  | 19 |  |  | 19
20 |  |  | 20 |  |  | 20
21 |  |  | 21 |  |  | 21
22 |  |  | 22 |  |  | 22
23 |  |  | 23 |  |  | 23
24 |  |  | 24 |  |  | 24
25 |  |  | 25 |  |  | 25
26 |  |  | 26 |  |  | 26
27 |  |  | 27 |  |  | 27
28 |  |  | 28 |  |  | 28
29 |  |  | 29 |  |  | 29
30 |  |  | 30 |  |  | 30
31 |  |  | 31 |  |  | 31
32 |  |  | 32 |  |  | 32
33 |  |  | 33 |  |  | 33
34 |  |  | 34 |  |  | 34
35 |  |  | 35 |  |  | 35
36 |  |  | 36 |  |  | 36
37 |  |  | 37 |  |  | 37
38 |  |  | 38 |  |  | 38
39 |  |  | 39 |  |  | 39
40 |  |  | 40 |  |  | 40
| THC/Iref (%) |  |  | THC/Iref (%) |  |  | THC/Iref (%)
THC |  |  | THC |  |  | THC
| PWHC/Iref (%) |  |  | PWHC/Iref (%) |  |  | PWHC/Iref (%)
PWHC |  |  | PWHC |  |  | PWHC
Manufacturer's EMC Test Report Filename
Manufacturer's EMC Test Report Document Number
Manufacturer's Documentation Declaration
In accordance with EN 61000-3-12… | [5 empty] | Minimum short-circuit level, Ssc min (kVA)
Declaration of Conformity
CE Declaration of Conformity Filename
CE Declaration of Conformity Document/Certificate Number
Standards Cited on CE Declaration of Conformity
Harmonic Standards
Voltage Fluctuation/Flicker Standards
Manufacturer's Declaration for Connection Design Purposes
Statement
Drop-down lists
Air Source
Ground Source
Water Source
1
Split
3
230
400
Whole system
Heat pump
Back-up heater - on-board
Back-up heater - external
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external
Equipment complying with IEC 61000-3-12
Equipment complying with IEC 61000-3-12 subject to minimum short-circuit power
EN 61000-3-12
EN 61000-3-2
EN 61000-6-3
EN 61000-6-4
EN 61000-3-11
EN 61000-3-3
EN 61000-6-3
EN 61000-6-4
Emissions do not exceed Class A limits in IEC 61000-3-2
Note on D117: Scarbro, Simon P.: Use Sheet A8 to provide supporting current emission data.

## A5_Data_>75A_Harmonics
A5 DATA ENTRY SHEET - >75A [Harmonics]
NOTE | Use this sheet to provide information and data for equipment falling outside the scope of IEC 61000-3-12 and IEC 61000-3-2.
NOTE | To enable the Network Operator to offer the most economic electrical connection design (using an EREC G5 Stage 2 assessment), it is necessary for the manufacturer to state harmonic current emissions.
CONFIDENTIAL DATA
Equipment
Make
Model
Model Reference
Heat Pump Type
Phases
Voltage (V)
Total Heat Pump System (Input) Rated Current (A)
Total Heat Pump System (Input) Rated Power (kVA)
Module
Module Input Rated Current (A)
Module Input Rated Power (kVA)
Harmonic Current Emission Data
Phase | L1 |  | Phase | L2 |  | Phase | L3
| Current (A) |  |  | Current (A) |  |  | Current (A)
Irated |  |  | Irated |  |  | Irated
| Current (A) | % Irated (%) |  | Current (A) | % Irated (%) |  | Current (A) | % Irated (%)
RMS |  |  | RMS |  |  | RMS
Harmonic h | Ih (A) |  | Harmonic h | Ih (A) |  | Harmonic h | Ih (A)
1 |  |  | 1 |  |  | 1
2 |  |  | 2 |  |  | 2
3 |  |  | 3 |  |  | 3
4 |  |  | 4 |  |  | 4
5 |  |  | 5 |  |  | 5
6 |  |  | 6 |  |  | 6
7 |  |  | 7 |  |  | 7
8 |  |  | 8 |  |  | 8
9 |  |  | 9 |  |  | 9
10 |  |  | 10 |  |  | 10
11 |  |  | 11 |  |  | 11
12 |  |  | 12 |  |  | 12
13 |  |  | 13 |  |  | 13
14 |  |  | 14 |  |  | 14
15 |  |  | 15 |  |  | 15
16 |  |  | 16 |  |  | 16
17 |  |  | 17 |  |  | 17
18 |  |  | 18 |  |  | 18
19 |  |  | 19 |  |  | 19
20 |  |  | 20 |  |  | 20
21 |  |  | 21 |  |  | 21
22 |  |  | 22 |  |  | 22
23 |  |  | 23 |  |  | 23
24 |  |  | 24 |  |  | 24
25 |  |  | 25 |  |  | 25
26 |  |  | 26 |  |  | 26
27 |  |  | 27 |  |  | 27
28 |  |  | 28 |  |  | 28
29 |  |  | 29 |  |  | 29
30 |  |  | 30 |  |  | 30
31 |  |  | 31 |  |  | 31
32 |  |  | 32 |  |  | 32
33 |  |  | 33 |  |  | 33
34 |  |  | 34 |  |  | 34
35 |  |  | 35 |  |  | 35
36 |  |  | 36 |  |  | 36
37 |  |  | 37 |  |  | 37
38 |  |  | 38 |  |  | 38
39 |  |  | 39 |  |  | 39
40 |  |  | 40 |  |  | 40
41 |  |  | 41 |  |  | 41
42 |  |  | 42 |  |  | 42
43 |  |  | 43 |  |  | 43
44 |  |  | 44 |  |  | 44
45 |  |  | 45 |  |  | 45
46 |  |  | 46 |  |  | 46
47 |  |  | 47 |  |  | 47
48 |  |  | 48 |  |  | 48
49 |  |  | 49 |  |  | 49
50 |  |  | 50 |  |  | 50
Manufacturer's EMC Test Report Filename
Manufacturer's EMC Test Report Document Number
Drop-down lists…
Air Source
Ground Source
Water Source
1
Split
3
230
400
Whole system
Heat pump
Back-up heater - on-board
Back-up heater - external
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external

## A6_Data_=<75A Fluctuations
A6 DATA ENTRY SHEET - ≤75A [Fluctuations]
NOTE | Use this sheet to provide information and data for equipment falling within the scope of IEC 61000-3-11.
DATA
Equipment
Make
Model
Model Reference
Heat Pump Type
Phases
Voltage (V)
Total Heat Pump System (Input) Rated Current (A)
Total Heat Pump System (Input) Rated Power (kVA)
Module
Module Input Rated Current (A)
Module Input Rated Power (kVA)
Manufacturer's Documentation Declaration
In accordance with EN 61000-3-11… |  | Maximum source impedance, Zmax (Ω)
Manufacturer's EMC Test Report Filename
Manufacturer's EMC Test Report Document Number
Drop-down lists
Air Source
Ground Source
Water Source
1
Split
3
230
400
Whole system
Heat pump
Back-up heater - on-board
Back-up heater - external
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external
Equipment complying with IEC 61000-3-3 technical requirements
Requires Zsource ≤Zmax
Requires Service Current Capacity ≥100A per phase
Not applicable

## A7_Data_>75A_Fluctuations
A7 DATA ENTRY SHEET - >75A [Fluctuations]
NOTE | Use this sheet to provide information and data for equipment falling outside of the scope of IEC 61000-3-11 and IEC 61000-3-3.
DATA
Equipment
Make
Model
Model Reference
Heat Pump Type
Phases
Voltage (V)
Total Heat Pump System (Input) Rated Current (A)
Total Heat Pump System (Input) Rated Power (kVA)
Module
Module Input Rated Current (A)
Module Input Rated Power (kVA)
Voltage Fluctuation and Flicker Data
Maximum source impedance to comply with IEC 61000-3-11 Section 5 limits (Ω)
Manufacturer's EMC Test Report Filename
Manufacturer's EMC Test Report Document Number
Drop-down lists
Air Source
Ground Source
Water Source
1
Split
3
230
400
Whole system
Heat pump
Back-up heater - on-board
Back-up heater - external
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external
Equipment complying with IEC 61000-3-3 technical requirements
Requires Zsource ≤Zmax
Requires Service Current Capacity ≥100A per phase
Not applicable

## A8_Data_>16A_Harmonics
A8 DATA ENTRY SHEET - >16A [Harmonics]
NOTE | Use this sheet to provide information and data for equipment falling outside the scope of IEC 61000-3-2 where compliance with the Class A limits of that standard is claimed.
CONFIDENTIAL DATA
Equipment
Make
Model
Model Reference
Heat Pump Type
Phases
Voltage (V)
Total Heat Pump System (Input) Rated Current (A)
Total Heat Pump System (Input) Rated Power (kVA)
Module
Module Input Rated Current (A)
Module Input Rated Power (kVA)
Harmonic Current Emission Data
Phase | L1 |  | Phase | L2 |  | Phase | L3
| Current (A) |  |  | Current (A) |  |  | Current (A)
Irated |  |  | Irated |  |  | Irated
| Current (A) |  |  | Current (A) |  |  | Current (A)
IRMS |  |  | IRMS |  |  | IRMS
Harmonic h | Ih max (A) | Ih ave (A) | Harmonic h | Ih max (A) | Ih ave (A) | Harmonic h | Ih max (A) | Ih ave (A)
1 |  |  | 1 |  |  | 1
2 |  |  | 2 |  |  | 2
3 |  |  | 3 |  |  | 3
4 |  |  | 4 |  |  | 4
5 |  |  | 5 |  |  | 5
6 |  |  | 6 |  |  | 6
7 |  |  | 7 |  |  | 7
8 |  |  | 8 |  |  | 8
9 |  |  | 9 |  |  | 9
10 |  |  | 10 |  |  | 10
11 |  |  | 11 |  |  | 11
12 |  |  | 12 |  |  | 12
13 |  |  | 13 |  |  | 13
14 |  |  | 14 |  |  | 14
15 |  |  | 15 |  |  | 15
16 |  |  | 16 |  |  | 16
17 |  |  | 17 |  |  | 17
18 |  |  | 18 |  |  | 18
19 |  |  | 19 |  |  | 19
20 |  |  | 20 |  |  | 20
21 |  |  | 21 |  |  | 21
22 |  |  | 22 |  |  | 22
23 |  |  | 23 |  |  | 23
24 |  |  | 24 |  |  | 24
25 |  |  | 25 |  |  | 25
26 |  |  | 26 |  |  | 26
27 |  |  | 27 |  |  | 27
28 |  |  | 28 |  |  | 28
29 |  |  | 29 |  |  | 29
30 |  |  | 30 |  |  | 30
31 |  |  | 31 |  |  | 31
32 |  |  | 32 |  |  | 32
33 |  |  | 33 |  |  | 33
34 |  |  | 34 |  |  | 34
35 |  |  | 35 |  |  | 35
36 |  |  | 36 |  |  | 36
37 |  |  | 37 |  |  | 37
38 |  |  | 38 |  |  | 38
39 |  |  | 39 |  |  | 39
40 |  |  | 40 |  |  | 40
41 |  |  | 41 |  |  | 41
42 |  |  | 42 |  |  | 42
43 |  |  | 43 |  |  | 43
44 |  |  | 44 |  |  | 44
45 |  |  | 45 |  |  | 45
46 |  |  | 46 |  |  | 46
47 |  |  | 47 |  |  | 47
48 |  |  | 48 |  |  | 48
49 |  |  | 49 |  |  | 49
50 |  |  | 50 |  |  | 50
Manufacturer's EMC Test Report Filename
Manufacturer's EMC Test Report Document Number
Drop-down lists…
Air Source
Ground Source
Water Source
1
Split
3
230
400
Whole system
Heat pump
Back-up heater - on-board
Back-up heater - external
Supplementary (boost) heater - on-board
Supplementary (boost) heater - external
Water (immersion) heater - on-board
Water (immersion) heater - external